## Summary Table
Iowa Energy Efficiency Statewide Technical Reference Manual - Version 5 (Effective Jan. 1, 2021)
Nonresidential Measures
Prepared by Vermont Energy Investment Corp.
Code, Title, Programs |  |  |  | Loadshape
Measure Code | End Use Category | Measure Title | Applicable Programs | Loadshape(s)
NR-AGE-CIRC-V04-210101 | Agricultural Equipment | Circulation Fans | TOS | Loadshape NREV06-Industrial Ventilation
NR-AGE-VENT-V03-210101 | Agricultural Equipment | Ventilation Fans | TOS | Loadshape NREV06-Industrial Ventilation
NR-AGE-HVLS-V03-210101 | Agricultural Equipment | High Volume Low Speed Fans | RF, NC | Loadshape– NREV06-Industrial Ventilation
NR-AGE-VCON-V02-210101 | Agricultural Equipment | Temperature Based On/Off Ventilation Controller | RF | Loadshape NREV06-Industrial Ventilation
NR-AGE-AMTO-V03-210101 | Agriculture | Automatic Milker Take Off |  | Loadshape NRE11 – Nonresidential Agriculture
NR-AGE-SCROL-V04-210101 | Agriculture | Dairy Scroll Compressor | RF | Loadshape NRE01 - Non-Residential Refrigeration - Grocery
NR-AGE-HTLP-V02-210101 | Agriculture | Heat Lamp |  | Loadshape C04 - Nonresidential Electric Heating
NR-AGE-HTRE-V04-210101 | Agriculture | Heat Reclaimer | RF | Loadshape C04 - Nonresidential Electric Heating
NR-AGE-HTMT-V03-210101 | Agriculture | Heat Mat |  | Loadshape C04 - Non-Residential Electric Heating
NR-AGE-GNDR-V02-200101 | Agriculture | Grain Dryer | TOS | Loadshape NRE11 – Non-Residential Agriculture
NR-AGE-LSWT-V02-180101 | Agriculture | Live Stock Waterer | TOS | Loadshape C04 - Nonresidential Electric Heating
NR-AGE-LIRR-V02-200101 | Agriculture | Low Pressure Irrigation |  | Loadshape NRE11 – Nonresidential Agriculture
NR-AGE-VDVP-V03-210101 | Agriculture | Variable Speed Frequency Drive for Dairy Vacuum Pump and Milking Machine | RF | Loadshape NRE11 – Non-Residential Agriculture
NR-AGE-DYPC-V05-210101 | Agriculture | Dairy Plate Cooler | RF | Loadshape NRE11 – Non-Residential Agriculture
NR-AGE-GROW-V01-210101 | Agriculture | LED Grow Light | TOS, NC, RF | Loadshape NRE11 – Non-Residential Agriculture
NR-AGE-GRAIN-V01-210101 | Agriculture | Grain Bin Fan Controls - Deemed | TOS, NC, RF | Loadshape NRE11 – Non-Residential Agriculture
NR-AGE-GRAIN-V01-210101 | Agriculture | Grain Bin Fan Controls - Custom | TOS, NC, RF | Loadshape NRE11 – Non-Residential Agriculture
NR-HWE-LFFA-V03-200101 | Hot Water | Low Flow Faucet Aerators | DI | Loadshape NREW01:16 - Nonresidential Electric Hot Water (by Building Type) Loadshape NRGW01:16 – Nonresidential Gas Hot Water (by Building Type)
NR-HWE-LFSH-V04-200101 | Hot Water | Low Flow Showerheads | DI | Loadshape NREW01:16 - Nonresidential Electric Hot Water (by Building Type) Loadshape NRGW01:16 – Nonresidential Gas Hot Water (by Building Type)
NR-HWE-GHWH-V05-210101 | Hot Water | Gas Hot Water Heater | TOS, NC, RF | Loadshape NRGW01:16 – Nonresidential Gas Hot Water (by Building Type)
NR-HWE-DHWC-V02-180101 | Hot Water | Controls for Central Domestic Hot Water | RF | Loadshape NREW08 – Nonresidential Electric Hot Water – Multifamily Loadshape NRGW08 – Nonresidential Gas Hot Water - Multifamily
NR-HWE-PCOV-V02-180101 | Hot Water | Pool Covers | TOS, RF, NC | Loadshape NRGW01:16 – Nonresidential Gas Hot Water (by Building Type)
NR-HWE-DWHR-V03-190101 | Hot Water | Drainwater Heat Recovery | NC, RF | Loadshape NREW01:16 – Nonresidential Electric Hot Water (by building type) Loadshape NRGW01:16 – Nonresidential Gas Hot Water (by Building Type)
NR-HVC-BOIL-V04-210101 | HVAC | Boiler | TOS, NC | Loadshape NRGH01:16 – Nonresidential Gas Heating (by Building Type) Loadshape NRGB01:16 – Nonresidential Gas Heat and Hot Water (by Building Type)
NR-HVC-FRNC-V04-200101 | HVAC | Furnace | TOS, NC | Loadshape NRGH01:16 – Nonresidential Gas Heating (by Building Type)
NR-HVC-FBLM-V03-200101 | HVAC | Furnace Blower Motor | TOS, RF, NC | Loadshape NREH01:16 - Nonresidential Electric Heat (by Building Type)
NR-HVC-HPSY-V03-200101 | HVAC | Heat Pump Systems | TOS, NC | Loadshape NREP01:16 - Nonresidential Electric Heat Pump (by Building Type)
NR-HVAC-GSHP-V03-200101 | HVAC | Geothermal Source Heat Pump | TOS, NC | Loadshape NREP01:16 - Nonresidential Electric Heat Pump (by Building Type)
NR-HVC-SPUA-V04-210101 | HVAC | Single-Package and Split System Unitary Air Conditioners | TOS, NC | NREC01:16 - Nonresidential Cooling (by Building Type)
NR-HVC-CHIL-V02-200101 | HVAC | Electric Chiller | TOS, NC | Loadshape NREC01:16 - Nonresidential Cooling (by Building Type)
NR-HVC-PTAC-V02-200101 | HVAC | Package Terminal Air Conditioner (PTAC) | TOS, NC, EREP | Loadshape NREP01:16 - Nonresidential Electric Heat Pump (by Building Type)
NR-HVC-PTAC-V02-200101 | HVAC | Package Terminal Heat Pump (PTHP) | TOS, NC, EREP | Loadshape NREP01:16 - Nonresidential Electric Heat Pump (by Building Type)
NR-HVC-GREM-V02-200101 | HVAC | Guest Room Energy Management (PTAC) | TOS, NC | Loadshape NREH07 – Nonresidential Electric Heat – Lodging Loadshape NRECH07 – Nonresidential Cooling – Lodging Loadshape NRGH07 – Nonresidential Gas Heating – Lodging
NR-HVC-BLRT-V02-200101 | HVAC | Boiler Tune-up | RF | Loadshape NRGH01:16 – Nonresidential Gas Heating (by Building Type) Loadshape NRGB01:16 – Nonresidential Gas Heat and Hot Water (by Building Type)
NR-HVC-FTUN-V03-200101 | HVAC | Furnace Tune-Up | RF | Loadshape NRGH01:16 – Nonresidential Gas Heating (by Building Type) Loadshape NREH01:16 – Nonresidential Electric Heating (by Building Type)
NR-HVC-PROG-V04-210101 | HVAC | Small Commercial Thermostats | RF, DI | Loadshape NREC17 – Non-Residential Cooling – Small Programmable Thermostat Loadshape NREP01:16 – Non-Residential Electric Heat Pump (by Building Type) Loadshape NRGH01:16 – Nonresidential Gas Heating (by Building Type)
NR-HVC-VFHP-V04-210101 | HVAC | Variable Frequency Drives for HVAC Pumps | TOS, RF | Loadshape NRE07 – VFD - Boiler feedwater pumps Loadshape NRE08 – VFD - Chilled water pumps Loadshape NRE09 – VFD - Boiler circulation pumps
NR-HVC-VFDF-V03-200101 | HVAC | Variable Frequency Drives for HVAC Supply and Return Fans | TOS, RF | Loadshape NRE04 – VFD - Supply fans Loadshape NRE05 – VFD - Return fans Loadshape NRE06 – VFD - Exhaust fans
NR-HVC-DUCT-V02-200101 | HVAC | Duct Insulation |  | NREC01:16 – Nonresidential Cooling (by Building Type) NREH01:16 – Nonresidential Electric Heat (by Building Type) NREP01:16 – Nonresidential Electric Heat Pump (by Building Type) NRGH01:16 – Nonresidential Gas Heating (by Building Type)
NR-HVC-DCTS-V02-200101 | HVAC | Duct Repair and Sealing - Blower Door | RF | NREC01:16 – Nonresidential Cooling (by Building Type) NREH01:16 – Nonresidential Electric Heat (by Building Type) NREP01:16 – Nonresidential Electric Heat Pump (by Building Type) NRGH01:16 – Nonresidential Gas Heating (by Building Type)
NR-HVC-DCTS-V02-200101 | HVAC | Duct Repair and Sealing - Deemed | RF | NREC01:16 – Nonresidential Cooling (by Building Type) NREH01:16 – Nonresidential Electric Heat (by Building Type) NREP01:16 – Nonresidential Electric Heat Pump (by Building Type) NRGH01:16 – Nonresidential Gas Heating (by Building Type)
NR-HVC-CPIN-V03-200101 | HVAC | Chiller Pipe Insulation | RF | NREC01:16 – Nonresidential Cooling (by Building Type)
NR-HVC-HPIN-V03-210101 | HVAC | Hydronic Heating Pipe Insulation | RF, DI | Loadshape NRGH01:16 – Nonresidential Gas Heating (by Building Type) Loadshape NRGB01:16 – Nonresidential Gas Heat and Hot Water (by Building Type)
NR-HVC-SODP-V02-200101 | HVAC | Shut Off Damper for Space Heating Boilers or Furnaces | RF | Loadshape NRGH01:16 – Nonresidential Gas Heating (by Building Type)
NR-HVC-RMAC-V02-190101 | HVAC | Room Air Conditioner | TOS | Loadshapes NREC01-NREC16 dependent on building type.
NR-APL-RACR-V02-180101 | HVAC | Room Air Conditioner Recycling | ERET | Loadshapes NREC01-NREC16 dependent on building type.
NR-HVC-STRE-V02-200101 | HVAC | Steam Trap Replacement or Repair | RF | Loadshape NRGH01:16 - Nonresidential Gas Heating (by Building Type)
NR-HVC-ACTU-V01-210101 | HVAC | Electric HVAC Tune-Up Custom | RF | Loadshape NREC01:16 - Nonresidential Cooling (by Building Type)
NR-HVC-ACTU-V01-210101 | HVAC | Electric HVAC Tune-Up Deemed | RF | Loadshape NREC01:16 - Nonresidential Cooling (by Building Type)
NR-LTG-STCFL-V01-170101 | Lighting | Compact Fluorescent Lamp - Standard | TOS, DI, RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type)
NR-LTG-SPCFL-V02-180101 | Lighting | Compact Fluorescent Lamp - Specialty | TOS, RF, DI | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type)
NR-LTG-LEDA-V05-210101 | Lighting | LED Lamp Standard | TOS, RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type)
NR-LTG-LEDS-V05-210101 | Lighting | LED Lamp Specialty | TOS, RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type)
NR-LTG-LDFX-V04-200101 | Lighting | LED Fixtures | TOS, RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type)
NR-LTG-T5HO-V02-200101 | Lighting | T5 HO Fixtures and Lamp/Ballast Systems | TOS, RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type)
NR-LTG-HPT8-V01-170101 | Lighting | High Performance and Reduced Wattage T8 Fixtures and Lamps | TOS, RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type)
NR-LTG-PSMH-V02-180101 | Lighting | Metal Halide | RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type)
NR-LTG-EXIT-V04-200101 | Lighting | Commercial LED Exit Sign | RF, DI | Loadshape E01 – Flat
NR-LTG-STLT-V01-190101 | Lighting | LED Street Lighting |  | Loadshape NREL017 – Nonresidential Street Lighting
NR-LTG-LDTP-V01-190101 | Lighting | LED Traffic and Pedestrian Signals | RF | Loadshape NREL18 - Traffic Signal - Red Balls, always changing or flashing Loadshape NREL19 - Traffic Signal - Red Balls, changing day, off night Loadshape NREL20 - Traffic Signal - Green Balls, always changing Loadshape NREL21 - Traffic Signal - Green Balls, changing day, off night Loadshape NREL22 - Traffic Signal - Red Arrows Loadshape NREL23 - Traffic Signal - Green Arrows Loadshape NREL24 - Traffic Signal - Flashing Yellows Loadshape NREL25 - Traffic Signal - “Hand” Don’t Walk Signal Loadshape NREL26 - Traffic Signal - “Man” Walk Signal Loadshape NREL27 - Traffic Signal - Bi-Modal Walk/Don’t Walk
NR-LTG-LICO-V01-210101 | Lighting | Lighting Control | TOS, RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type)
NR-LTG-DAYC-V03-200101 | Lighting | Daylighting Control | TOS, RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type)
NR-LTG-MLLS-V03-200101 | Lighting | Multi-Level Lighting Switch | RF | Loadshape NREL01:16 – Nonresidential Lighting (by Building Type)
NR-MSC-VFDP-V03-200101 | Miscellaneous | Variable Frequency Drives for Process | TOS, RF | Custom Loadshape
NR-MSC-CLWA-V02-190101 | Miscellaneous | Clothes Washer | TOS, NC | Loadshape RE01 - Residential Clothes Washer Loadshape G01 - Flat (gas)
NR-MCS-MOTR-V03-200101 | Miscellaneous | Motors | TOS | Loadshape NRE03 – Non-Residential Industrial Motor
NR-MSC-BACH-V01-180101 | Miscellaneous | Forklift Battery Charger | TOS, NC | Loadshape NRE13 - Indust. 1-shift (8/5) Loadshape NRE14 - Indust. 2-shift (16/5) Loadshape NRE15 - Indust. 3-shift (24/5) Loadshape NRE16 - Indust. 4-shift (24/7)
NR-FSE-DISH-V02-190101 | Food Service | Dishwasher | TOS | Loadshape NREW12 - Nonresidential Electric Hot Water – Restaurant Loadshape NRGW12 - Nonresidential Gas Hot Water – Restaurant
NR-FSE-CSGD-V01-190101 | Food Service | Commercial Solid and Glass Door Refrigerators & Freezers | TOS | Loadshape NRE01 - Nonresidential Refrigeration – Grocery
NR-FSE-SPRY-V03-200101 | Food Service | Pre-Rinse Spray Valve | TOS, DI | Loadshape NREW12 - Nonresidential Electric Hot Water – Restaurant Loadshape NRGW12 - Nonresidential Gas Hot Water – Restaurant
NR-FSE-IRUB-V01-170101 | Food Service | Infrared Upright Broiler | TOS | Loadshape NRGC01 - Nonresidential Gas Cooking – Restaurant
NR-FSE-IRBL-V01-170101 | Food Service | Infrared Salamander Broiler | TOS | Loadshape NRGC01 - Nonresidential Gas Cooking – Restaurant
NR-FSE-IRCB-V01-170101 | Food Service | Infrared Charbroiler | TOS | Loadshape NRGC01 - Nonresidential Gas Cooking – Restaurant
NR-FSE-ESCV-V01-170101 | Food Service | Convection Oven | TOS | Loadshape NRE02 - Nonresidential Electric Cooking – Restaurant Loadshape NRGC01 - Nonresidential Gas Cooking – Restaurant
NR-FSE-CVOV-V03-210101 | Food Service | Conveyor Oven | TOS | Loadshape NRGC01 - Nonresidential Gas Cooking – Restaurant
NR-FSE-IROV-V01-170101 | Food Service | Infrared Rotisserie Oven | TOS | Loadshape NRGC01 - Nonresidential Gas Cooking – Restaurant
NR-FSE-STMC-V02-190101 | Food Service | Commercial Steam Cooker | TOS | Loadshape NRE02 - Nonresidential Electric Cooking – Restaurant Loadshape NRGC01 - Nonresidential Gas Cooking – Restaurant
NR-FSE-ESFR-V02-190101 | Food Service | Fryer | TOS | Loadshape NRE02 - Nonresidential Electric Cooking – Restaurant Loadshape NRGC01 - Nonresidential Gas Cooking – Restaurant
NR-FSE-ESGR-V01-170101 | Food Service | Griddle | TOS | Loadshape NRE02 - Nonresidential Electric Cooking – Restaurant Loadshape NRGC01 - Nonresidential Gas Cooking – Restaurant
NR-SHL-AIRS-V04-210101 | Shell | Infiltration Control - Blower Door | RF | NREC01:16 – Nonresidential Cooling (by Building Type) NREH01:16 – Nonresidential Electric Heat (by Building Type) NREP01:16 – Nonresidential Electric Heat Pump (by Building Type) NRGH01:16 – Nonresidential Gas Heating (by Building Type)
NR-SHL-AIRS-V04-210101 | Shell | Infiltration Control - Deemed | RF | NREC01:16 – Nonresidential Cooling (by Building Type) NREH01:16 – Nonresidential Electric Heat (by Building Type) NREP01:16 – Nonresidential Electric Heat Pump (by Building Type) NRGH01:16 – Nonresidential Gas Heating (by Building Type)
NR-SHL-FINS-V04-210101 | Shell | Foundation Wall Insulation | RF, NC | NREC01:16 – Nonresidential Cooling (by Building Type) NREH01:16 – Nonresidential Electric Heat (by Building Type) NREP01:16 – Nonresidential Electric Heat Pump (by Building Type) NRGH01:16 – Nonresidential Gas Heating (by Building Type)
NR-SHL-XINS-V05-210101 | Shell | Roof Insulation | RF, NC | NREC01:16 – Nonresidential Cooling (by Building Type) NREH01:16 – Nonresidential Electric Heat (by Building Type) NREP01:16 – Nonresidential Electric Heat Pump (by Building Type) NRGH01:16 – Nonresidential Gas Heating (by Building Type)
NR-SHL-WINS-V03-210101 | Shell | Wall Insulation | RF, NC | NREC01:16 – Nonresidential Cooling (by Building Type) NREH01:16 – Nonresidential Electric Heat (by Building Type) NREP01:16 – Nonresidential Electric Heat Pump (by Building Type) NRGH01:16 – Nonresidential Gas Heating (by Building Type)
NR-SHL-WIND-V05-210101 | Shell | Efficient Windows | NC, TOS | NREC01:16 – Nonresidential Cooling (by Building Type) NREH01:16 – Nonresidential Electric Heat (by Building Type) NREP01:16 – Nonresidential Electric Heat Pump (by Building Type) NRGH01:16 – Nonresidential Gas Heating (by Building Type)
NR-SHL-DOOR-V05-210101 | Shell | Insulated Doors | RF | NREC01:16 – Nonresidential Cooling (by Building Type) NREH01:16 – Nonresidential Electric Heat (by Building Type) NREP01:16 – Nonresidential Electric Heat Pump (by Building Type) NRGH01:16 – Nonresidential Gas Heating (by Building Type)
NR-RFG-CLOS-V01-190101 | Refrigeration | LED Refrigerator Case Light Occupancy Sensor | RF | Loadshape NREL01 – Nonresidential Lighting – Convenience Loadshape NREL03 – Nonresidential Lighting – Grocery Loadshape NREL13 – Nonresidential Lighting – Retail – Large Loadshape NREL14 – Nonresidential Lighting – Retail – Small
NR-RFG-DHCT-V02-180101 | Refrigeration | Door Heater Controls for Cooler or Freezer | RF | Loadshape NRE01 - Nonresidential Refrigeration – Grocery
NR-RFG-ECMF-V03-190101 | Refrigeration | Efficient Motors for Walk-in and Display Case Coolers / Freezers | RF | Loadshape NRE01 - Nonresidential Refrigeration – Grocery
NR-RFG-NCOV-V02-180101 | Refrigeration | Night Covers for Open Refrigerated Display Cases | RF | Loadshape NRE12: Night Covers for Refrigeration Display Cases
NR-RFG-ESVE-V03-210101 | Refrigeration | Refrigerated Beverage Vending Machine | TOS | Loadshape NRE01 - Nonresidential Refrigeration – Grocery
NR-REF-RFRC-V02-200101 | Refrigeration | Refrigerator Recycling - Regression | ERET | Loadshape RE09 - Residential Refrigerator Loadshape RE02 – Residential Freezer
NR-REF-RFRC-V02-200101 | Refrigeration | Refrigerator Recycling - Deemed | ERET | Loadshape RE09 - Residential Refrigerator Loadshape RE02 – Residential Freezer
NR-REF-RFRC-V02-200101 | Refrigeration | Freezer Recycling - Regression | ERET | Loadshape RE09 - Residential Refrigerator Loadshape RE02 – Residential Freezer
NR-REF-RFRC-V02-200101 | Refrigeration | Freezer Recycling - Deemed | ERET | Loadshape RE09 - Residential Refrigerator Loadshape RE02 – Residential Freezer
NR-RFG-SCR-V02-190101 | Refrigeration | Scroll Refrigeration Compressor | RF | Loadshape NRE01 - Non-Residential Refrigeration – Grocery
NR-RFG-STCR-V03-190101 | Refrigeration | Strip Curtain for Walk-in Coolers and Freezers | RF | Loadshape NRE01 - Nonresidential Refrigeration – Grocery
NR-RFG-ESIM-V02-190101 | Refrigeration | Ice Maker | TOS | Loadshape NRE01 - Nonresidential Electric Refrigeration – Restaurant
NR-RFG-ECMC-V01-190101 | Refrigeration | Efficient Motor Controls for Walk-in and Display Case Coolers/Freezers | RF | Loadshape NRE01 - Non-Residential Refrigeration – Grocery
NR-RFG-DOOR-V01-210101 | Refrigeration | Add Doors to Display Cases | RF | Loadshape NRE01 - Nonresidential Refrigeration – Grocery Loadshape NREC01:16 - Nonresidential Cooling (by Building Type) Loadshape NRGH01:16 – Nonresidential Gas Heating (by Building Type)
NR-RFG-ECON-V01-210101 | Refrigeration | Refrigeration Economizers | RF | Loadshape NRE17 – Refrigeration Economizer
NR-MSC-VSDA-V01-210101 | Compressed Air | Air Compressor with VSD | TOS | Loadshape NRE13 – Indust. 1-shift (8/5) Loadshape NRE14 – Indust. 2-shift (16/5) Loadshape NRE15 – Indust. 3-shift (24/5) Loadshape NRE16 – Indust. 4-shift (24/7)
NR-MSC-ACNZ-V01-210101 | Compressed Air | High Efficiency Air Nozzle | RF | Loadshape NRE13 – Indust. 1-shift (8/5) Loadshape NRE14 – Indust. 2-shift (16/5) Loadshape NRE15 – Indust. 3-shift (24/5) Loadshape NRE16 – Indust. 4-shift (24/7)
NR-MSC-NLCD-V01-210101 | Compressed Air | No Loss Condensate Drain | RF | NRE03 – Industrial Motor

## BLANK
BLANK
Measure Code:
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition

## Circulation Fans
Circulation Fans
| Measure Code: | NR-AGE-CIRC-V04-210101
| Lifetime of Efficient Equipment: | [7 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime | [5 empty] | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
10
| Measure Cost: | [7 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Install Cost | Full Cost (Early Replacement) |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known | Fan Diameter | 12-23 | Actual - $375
|  |  |  | 24-35 | Actual - $450
|  |  |  | 36-47 | Actual - $525
|  |  |  | 48+ | Actual - $600
|  | Unknown |  |  | 150
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([WattsBase] - [WattsEE]) / 1000 * [Hours] * [Nfans]
| Time of Sale Demand (ΔkW) | =([WattsBase] - [WattsEE]) / 1000 * [CF] * [ Nfans]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Fan Diameter | 12-23 |  |  | 366 | N | Watts | Demand (W) of baseline fan
|  |  | 24-35 |  |  | 615
|  |  | 36-47 |  |  | 810
|  |  | 48+ |  |  | 1358
| [WattsEE] | Fan Diameter | 12-23 |  |  | 298 | N | Watts | Demand (W) of efficient fan
|  |  | 24-35 |  |  | 440
|  |  | 36-47 |  |  | 529
|  |  | 48+ |  |  | 993
| [Hours] | Facility Type | Hog |  |  | 3597 | Y | Hours | Actual hours of operation. Typically the fans will be operated above certain temperature thresholds, and therefore the operating hours can be reasonably estimated using the Ag Ventilation Operating Hours Calculator if temperature setpoints are known. If not, the following table can be used to establish operating hours by facility type (hog, poultry, or dairy). For dairy facilities the typical temperature setpoint can be assumed to be 67⁰F, for poultry and hog facilities it can be assumed to be 65⁰F and 60⁰F, respectively, as these are the recommended temperatures above which comfort cooling should be provided for livestock .
|  |  | Poultry |  |  | 2862
|  |  | Dairy |  |  | 2578
|  |  | Unknown/Other |  |  | 3249
| [Nfans] | [5 empty] | Y |  | Number of circulation fans
| [CF] |  |  |  |  | 100% | N |  | Summer Peak Coincidence Factor

## Ventilation Fans
Ventilation Fans
| Measure Code: | NR-AGE-VENT-V03-210101
| Lifetime of Efficient Equipment: | [7 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime | [5 empty] | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
7
| Measure Cost: | [7 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Install Cost | Full Cost (Early Replacement) |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known | Fan Diameter | 12-23 | Actual - $375
|  |  |  | 24-35 | Actual - $450
|  |  |  | 36-47 | Actual - $525
|  |  |  | 48+ | Actual - $600
|  | Unknown |  |  | 150
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([WattsBase] - [WattsEE]) / 1000 * [Hours] * [Nfans]
| Time of Sale Demand (ΔkW) | =([WattsBase] - [WattsEE]) / 1000 * [CF] * [ Nfans]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Fan Diameter | 14-23 |  |  | 382 | N | Watts | Demand (W) of baseline fan
|  |  | 24-35 |  |  | 550
|  |  | 36-47 |  |  | 879
|  |  | 48+ |  |  | 1353
| [WattsEE] | Fan Diameter | 14-23 |  |  | 304 | N | Watts | Demand (W) of efficient fan
|  |  | 24-35 |  |  | 383
|  |  | 36-47 |  |  | 565
|  |  | 48+ |  |  | 1041
| [Hours] | Facility Type | Hog |  |  | 4923 | Y | Hours | Actual hours of operation. Typically the fans will be operated in a staged fashion such that only a fraction of total fans are operating in conditions that do not require maximum installed capacity. Accordingly, effective full load hours (EFLH) should be determined based on operating schedule and considering factors such as number of fans, stages, and temperature band definitions. If this information is unavailable, the table below may be used to reasonably estimate EFLH for hog, poultry, and dairy facilities, based on typical control schedules
|  |  | Poultry |  |  | 4794
|  |  | Dairy |  |  | 4205
|  |  | Unknown/Other |  |  | 4800
| [Nfans] | [5 empty] | Y |  | Number of circulation fans
| [CF] |  |  |  |  | 100% | N |  | Summer Peak Coincidence Factor

## High Volume Low Speed Fans
High Volume Low Speed Fans
| Measure Code: | NR-AGE-HVLS-V03-210101
| Lifetime of Efficient Equipment: | [7 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime | [5 empty] | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
10
| Measure Cost: | [7 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Install Cost | Full Cost (Early Replacement) |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known | Fan Diameter | 16-17.9 | Actual - $1,210 | Actual
|  |  |  | 18-19.9 | Actual - $1,460
|  |  |  | 20-23.9 | Actual - $1,840
|  |  |  | 24+ | Actual - $2,090
|  | Unknown | Fan Diameter | 16-17.9 | 4100
|  |  |  | 18-19.9 | 4130
|  |  |  | 20-23.9 | 4190
|  |  |  | 24+ | 4230
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =(∑ ([N_base] * [WattsBase]) - ∑([N_ee] *[WattsEE])) / 1000 * [Hours]
| Time of Sale Demand (ΔkW) | =(∑([N_base] * [WattsBase])-∑([N_ee] * [WattsEE)])/1000 * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Nbase] | Retrofit |  |  |  |  | Y |  | Number of baseline (conventional) fans being replaced (of equivalent wattage)
New Construction
| [Wattsbase] | Project Type | New Construction | Diameter of Fan (ft) | 16-17.9 | 4497 | Y | Watts | Operating demand (W) of baseline fan
[5 empty] | 18-19.9 | 5026
[5 empty] | 20-23.9 | 5555
[5 empty] | 24+ | 6613
Retrofit
| [Nee] | [5 empty] | Y |  | Number of efficient fans installed (of equivalent wattage)
| [Wattsee] | Diameter of Fan | 16-17.9 | Type | New Construction | 761 | Y | Watts | Operating demand (W) of efficient fan
|  |  | 18-19.9 |  |  | 850
|  |  | 20-23.9 |  |  | 940
|  |  | 24+ |  |  | 1119
Retrofit
| [Hours] | Facility Type | Hog |  |  | 3597 | Y | Hours | Actual hours of operation. Typically the fans will be operated above certain temperature thresholds, and therefore the operating hours can be reasonably estimated using the Ag Ventilation Operating Hours Calculator if temperature setpoints are known. If not, the following table can be used to establish operating hours by facility type (hog, poultry, or dairy). For dairy facilities the typical temperature setpoint can be assumed to be 67⁰F, for poultry and hog facilities it can be assumed to be 65⁰F and 60⁰F, respectively, as these are the recommended temperatures above which comfort cooling should be provided for livestock .
|  |  | Poultry |  |  | 2862
|  |  | Dairy |  |  | 2578
|  |  | Unknown/Other |  |  | 3259
| [CF] |  |  |  |  | 100% | N |  | Summer Peak Coincidence Factor

## Temp. Based On Off Vent. Contr.
Temp. Based On Off Vent. Contr.
| Measure Code: | NR-AGE-VCON-V02-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
7
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([Watts_fan]) / 1000 * ([Hours_control] )
Time of Sale Demand (ΔkW)
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Watts_fan] | Diamter of Fan | 14-23 |  |  | 382 | Y | Watts | Total wattage of controlled fans
|  |  | 24-35 |  |  | 550
|  |  | 36-47 |  |  | 879
|  |  | 48+ |  |  | 1353
| [Hourscontrol] | Facility Type | Hog |  |  | 1384 | N | Hours | Reduction in fan run hours due to controller
|  |  | Poultry |  |  | 877
|  |  | Dairy |  |  | 624
|  |  | Unknown/Other |  |  | 1137

## Auto Milker Take Off
Auto Milker Take Off
| Measure Code: | NR-AGE-AMTO-V03-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
10
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [kWh/cow/milking] * [Nmilkings] * [Ncows]
| Time of Sale Demand (ΔkW) | = [∆kWh] / [FLH] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [kWh/Cow] |  |  |  |  | 50 | N |  | kWh used per cow per milking
| [Nmilkings] |  |  |  |  | 2 | Y |  | Number of milkings per day
| [Ncows] |  |  |  |  | 140 | Y |  | Number of milking cows per farm
| [FLH] |  |  |  |  | 2703 | N |  | Full Load Hours
| [CF] |  |  |  |  | 0.793 | N |  | Coincidence Factor

## Dairy Scroll Compressor
Dairy Scroll Compressor
| Measure Code: | NR-AGE-SCROL-V04-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
12
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =(1/[EER_base] - 1/[EER_ee] ) * [Gal] * [Days_yr] * [Specific_heat] * [Density_milk] * [∆T] * 1/[1000] * [N_Cows]
| Time of Sale Demand (ΔkW) | = [∆kWh] / [FLH] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [EERBase] | Capacity | 0-7500 |  |  | 8.14 | Y | Btu/watt-hour | Cooling efficiency of existing compressor in Btu/watt-hour
|  |  | 7500-14999 |  |  | 9.28
|  |  | 15000-22499 |  |  | 10.64
|  |  | 22500-29999 |  |  | 11.18
|  |  | 30000-37499 |  |  | 11.12
|  |  | 37500-44999 |  |  | 11.74
|  |  | 45000-52499 |  |  | 11.68
|  |  | 52500-59999 |  |  | 12.54
|  |  | 60000-67499 |  |  | 12.46
|  |  | 67500-75000 |  |  | 11.44
| [EERee ] | Capacity | 0-7500 |  |  | 9.03 | Y | Btu/watt-hour | Cooling efficiency of efficient scroll compressor in Btu/watt-hour
|  |  | 7500-14999 |  |  | 10.86
|  |  | 15000-22499 |  |  | 11.83
|  |  | 22500-29999 |  |  | 12.15
|  |  | 30000-37499 |  |  | 12.39
|  |  | 37500-44999 |  |  | 12.7
|  |  | 45000-52499 |  |  | 12.52
|  |  | 52500-59999 |  |  | 13.12
|  |  | 60000-67499 |  |  | 13.13
|  |  | 67500-75000 |  |  | 12.37
| [Gal] |  |  |  |  | 6 | N | Gallons | Gallons of mile produced by one cow in a day
| [Daysyr] |  |  |  |  | 365.25 | N | Days | Number of days per year
| [Specificheat] |  |  |  |  | 0.93 | N | Btu/lb-°F | Specific heat of milk in Btu/lb-°F
| [Densitymilk] |  |  |  |  | 8.6 | N | lb/gal | Density milk in lb/gal
| [ΔT] | Pre-cooler? | Yes |  |  | 19 | N | °F | Required change in temperature
|  |  | No |  |  | 59
| [1000] |  |  |  |  | 1000 | N |  | Conversion factor from watts to kilowatts
| [Ncows] |  |  |  |  | 140 | Y |  | Number of milking cows per farm
| [FLH] |  |  |  |  | 3910 | N |  | Full load hours. The refrigeration is assumed to be in operation every day of the year, but because of compressor cycling the full load hours are 3910 hours for medium temperature applications
| [CF] |  |  |  |  | 96.4% | N |  | Summer Peak Coincidence Factor

## Heat Lamp
Heat Lamp
| Measure Code: | NR-AGE-HTLP-V02-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
1
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
0
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = ([W_Base] - [W_Eff]) / [1000] * [Hours] * [N_Units]
| Time of Sale Demand (ΔkW) | = 0
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Wbase] |  |  |  |  | 175 | N | watts | Wattage of baseline heat lamp
| [Weff] |  |  |  |  | 125 | Y | watts | Wattage of reduced wattage heat lamp
| [Hours] |  |  |  |  | 5105 | N | hours | Annual heat lamp operating hours
| [1000] |  |  |  |  | 1000 | N | Factor | Conversion factor from watts to kilowatts
| [Nunits] | [5 empty] | Y | Number | Number of units installed

## Heat Reclaimer
Heat Reclaimer
| Measure Code: | NR-AGE-HTRE-V04-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh/cow) | =[Reclaimable Heat] * (1 / [E.F]) / [3412]
| Time of Sale Demand (ΔkW) | = 0
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [Heat Available] |  |  | = [Lbs of Milk] * [CP,Milk] * [ΔTMilk]* [Days]
| [Heat Storage] |  |  | = [Hot Water] * [PWater] * [CP,Water] * [ΔTWater]* [Days]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Reclaimable Heat] | Precooler (Y/N)? | Heat Storage (No precooler) |  |  | 468229 | N | Btuh/cow/yr | Quantity of reclaimable heat per cow. These equations, for the reclaimable heat available from the milk (Heat Available) and for the heat required for the hot water needs for the dairy (Heat Storage), reveal that the heat available from the milk limits the usable heat when a precooler is installed. In the absence of a precooler, the heat storage limits the usable heat,
|  |  | Heat Available (precooler) |  |  | 332797 | N | Btuh/cow/yr
| [E.F] |  |  |  |  | 0.9 | Y |  | Energy factor of the electric water heater
| [3412] |  |  |  |  | 3412 | N | kWh/Btu | Btu to kWh electric conversion factor
| [Lbs of Milk] |  |  |  |  | 51.6 | Y | lbs/cow/day | Pounds of milk produced per day per cow that needs to be cooled
| [CP,Milk] |  |  |  |  | 0.93 | N | Btu/(lb-°F) | Specific heat of milk
| [ΔTMilk] | Precooler (Y/N)? | Yes (No precooler) |  |  | 59 | N | °F | Required change in temperature
|  |  | No (precooler) |  |  | 19
| [Days] |  |  |  |  | 365 | N | days/yr | Number of milking days per year
| [Hot Water] |  |  |  |  | 2.2 | N | gallons/cow/day | Gallons of hot water needed per cow per day
| [Pwater] |  |  |  |  | 8.33 | N | lbs/gallon | Density of water
| [CP,Water] |  |  |  |  | 1 | N | Btu/(lb-°F) | Specific heat of water
| [ΔTWater] |  |  |  |  | 70 | N | °F | Change in water temperature between the incoming water and the hot water leaving the hot water heater

## Heat Mat
Heat Mat
| Measure Code: | NR-AGE-HTMT-V03-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
5
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
225
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [([Mats_Single] * [Savings_SingleMat] )+ ([Mats_Double * [Savings_DoubleMat] )] -[ Controller] * [Controller Impact]
| Time of Sale Demand (ΔkW) | = 0
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [MatsSingle] | [5 empty] | Y | Number | Number of single mats at 90 watts or less
| [MatsDouble] | [5 empty] | Y | Number | Number of single mats at 180 watts or less
| [SavingsSingleMat] | Baseline Heat Lamp | 125W |  |  | 338 | N | kWh/mat | kWh per single mat
|  |  | 175W |  |  | 657
| [SavingsDoubleMat] | Baseline Heat Lamp | 125W |  |  | 817 | N | kWh/mat | kWh per double mat
|  |  | 175W |  |  | 1327
| [Controller] | [5 empty] | Y | Number | Number of Controllers
| [Controller Impact] |  |  |  |  | 383 | N | kWh | Usage per controller

## Grain Dryer
Grain Dryer
| Measure Code: | NR-AGE-GNDR-V02-200101
| Lifetime of Efficient Equipment: | [7 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime | [5 empty] | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: | [7 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Bushels per hour | < 500 | Annual bushels | < 170,000 | 20000
|  | ≥ 500 and < 1000 |  | ≥ 170,000 and < 330,000 | 30000
|  | ≥ 1000 and < 2000 |  | ≥ 330,000 and < 670,000 | 40000
|  | ≥ 2000 and < 3500 |  | ≥ 670,000 and < 1,200,000 | 70000
|  | ≥ 3500 and ≤ 5000 |  | ≥ 1,200,000 and ≤ 1,700,000 | 100000
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [Bushels_yr] )* ([kWh_Bushel old]) - [kWh_Bushel new])
Time of Sale Demand (ΔkW)
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Bushelsyr] | Savings Tier (Bushels/hr) from manufacturer | < 500 | Savings Tier (Bushels/yr) | < 170,000 | 85000 | Y | Number | Number of average bushels dried per year
|  |  | ≥ 500 and < 1000 |  | ≥ 170,000 and < 330,000 | 225000
|  |  | ≥ 1000 and < 2000 |  | ≥ 330,000 and < 670,000 | 400000
|  |  | ≥ 2000 and < 3500 |  | ≥ 670,000 and < 1,200,000 | 9000000
|  |  | ≥ 3500 and ≤ 5000 |  | ≥ 1,200,000 and ≤ 1,700,000 | 1400000
| [kWhBushel old] |  |  |  |  | 0.075 | N | kWh | kWh usage per bushel for an old grain dryer
| [kWhBushel new] |  |  |  |  | 0.035 | N | kWh | kWh usage per bushel for a new grain dryer

## Live Stock Waterer
Live Stock Waterer
| Measure Code: | NR-AGE-LSWT-V02-180101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
10
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known | Actual
|  | Unknown | 787.5
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =[kWh/waterer] * [N_Units]
Time of Sale Demand (ΔkW)
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [kWh/Waterer] |  |  |  |  | 1104 | N | kWh | kWh per waterer
| [Nunits] | [5 empty] | Y | Number | Number of waterers installed per farm

## Low Pressure Irrigation
Low Pressure Irrigation
| Measure Code: | NR-AGE-LIRR-V02-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
5
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =0.746 * [hours] * ([Pressure] * [Flow/Acre] * [Acres]) / ([1715] * [Pump_eff])
| Time of Sale Demand (ΔkW) | = [∆kWh] / [FLH] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Hours] |  |  |  |  | 864 | N | hrs/yr | Hours irrigation system runs per season
| [Pressure] | [5 empty] | Y | psi | Reduction in pump pressure resulting from retrofit
| [Acres] | [5 empty] | Y | Acres | Actual
| [Flow per Acre] |  |  |  |  | 5 | N | gallons/minute/acre | Flow rate per acre
| [1715] |  |  |  |  | 1715 | N |  | Conversion factor from PSI * GPM ((lb * gallons) / (sq. in * min)) to horsepower
| [Pumpeff] |  |  |  |  | 0.7 | Y |  | Pump efficiency
| [FLH] |  |  |  |  | 6768 | N |  | Full load hours
| [CF] |  |  |  |  | 79.3% | N |  | Summer System Peak Conincidence Factor

## VFD Dairy Vac Pump Milk Machine
VFD Dairy Vac Pump Milk Machine
| Measure Code: | NR-AGE-VDVP-V03-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Material and Labor Cost |  | Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [16] * [Nmilking] * [Ncows]
| Time of Sale Demand (ΔkW) | = [∆kWh] / [FLH] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [16] |  |  |  |  | 16 | N | kWh/cow | Annual energy savings per cow per milking from VSD dairy vacuum pump (kWh/cow/milking)
| [Nmilking] |  |  |  |  | 2 | Y | Milkings | Number of milkings per cow per day
| [Ncows] |  |  |  |  | 140 | Y | Number | Number of milking cows per farm
| [FLH] |  |  |  |  | 2703 | N | Hours | Full load hours
| [CF] |  |  |  |  | 79.3% | N |  | Coincidence Factor

## Dairy Plate Cooler
Dairy Plate Cooler
| Measure Code: | NR-AGE-DYPC-V05-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known (Y/N)? | Known | Actual
|  | Unknown | 3444
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [kWh/Cow] * [Ncows]
| Time of Sale Demand (ΔkW) | = [∆kWh] / [FLH] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [kWh/Cow] |  |  | =([Days] * [CP,Milk] * [Lbs of Milk] * [ΔT] - [Btuh of Heat Recovery]) * (1 / [EER]) * (1 / [1000])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [kWh/Cow] | Equipment Type | Installed alone |  |  | 76.2 | C | kWh/cow/yr | Per cow annual energy savings from plate-style milk precooler in kWh/cow/yr
|  |  | Heat reclaimer installed w/ electric hot water heater |  |  | 62
|  |  | Scroll compressor installed |  |  | 52.9
|  |  | Both heat reclaimer (with electric hot water heater) and scroll comrepssor installed |  |  | 65
|  |  | Default if type not known |  |  | 66.5
| [Ncows] |  |  |  |  | 140 | Y | Number | Number of milking cows per farm
| [Days] |  |  |  |  | 365 | N | Days | Number of days in a year
| [CP,Milk] |  |  |  |  | 0.93 | N | Btu/lb-°F | Specific heat of milk
| [Lbs of Milk] |  |  |  |  | 51.6 | Y | lbs/cow/day | Pounds of milk produced per day per cow that needs to be cooled
| [∆T] |  |  |  |  | 40 | Y | °F | Temperature reduction of the milk across precooler
| [Btuh of Heat Recovery] | Hot Water Heating Equipment | Non-Electric Water Heater |  |  | 0 | N | Btuh/cow/year | Difference in Btuh per cow per year recovered by heat reclaimer system (with and without precooler)
|  |  | Electric Water Heater and Heat Reclaimer |  |  | 131562
| [1000] |  |  |  |  | 1000 | N | W/kW | Conversion factor from watts to kilowatts
| [EER] | Compressor Type | Unknown compressor type |  |  | 9.3 | N |  | Energy Efficiency Ratio; efficiency of the existing compressor on the milk refrigeration system
|  |  | Reciprocating compressor |  |  | 8.4
|  |  | Scroll compressor |  |  | 10.9
| [FLH] |  |  |  |  | 3910 | N |  | Full load hours
| [CF] |  |  |  |  | 79% | N |  | Coincidence Factor

## LED Grow Light
LED Grow Light
| Measure Code: | NR-AGE-GROW-V01-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
9.5
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
See Sub-Algorithm
| O&M Cost: | Please see reference tables in 3.1.15
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = ([WattsBase] - [WattsEE]) * [Area] * [Hours] * [WHFe] / [1000] + [ΔkWh_Heating Penalty]
| Time of Sale Demand (ΔkW) | = ([WattsBase] - [WattsEE]) * [Area] * [CF] * [WHFd] / [1000]
| Time of Sale Gas (ΔTherms) | = ([WattsBase] - [WattsEE]) * [Area] * [Hours] * - [IFTherms] / [1000]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| Incremental Cost |  |  | = ([$1.42] * [WattsLED]) - [$65]
| [ΔkWh_Heating Penalty] |  |  | = ([WattsBase] - [WattsEE]) * [Area] * [Hours] * (- [IFkWh]) / [1000]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [$1.42] |  |  |  |  | 1.42 | N | $/W | LED fixture wattage to incremental cost conversion factor
| [$65] |  |  |  |  | 65 | N | $ | LED fixture wattage to incremental cost offset
| [WattsLED] | [5 empty] | Y | W | LED fixture wattage
| [Area] |  |  |  |  | 16 | Y | sqft | Illuminated grow area, in square feet, of active and growing space canopy
| [Hours] | Crop Type | Flowering Crops |  |  | 4200 | Y | Hours | Annual hours of operation
|  |  | Vegetative/Propogation Crops |  |  | 6300
|  |  | Microgreens |  |  | 6300
|  |  | Cannabis - Flowering Stage |  |  | 4200
|  |  | Other |  |  | 3650
|  |  | Average |  |  | 5250
| [1000] |  |  |  |  | 1000 | N | W/kW | Conversion from watts to kilowatts (W / kW)
| [WHFe] | HVAC Cooling Type | Cooling |  |  | 1.06 | N |  | Waste heat factor for energy to account for cooling energy savings from efficient lighting
|  |  | No Cooling |  |  | 1
| [WattsBase] | Crop Type | Flowering Crops (Tomatoes and Peppers) |  |  | 68.8 | Y | W/sqft | Baseline wattage per square foot of coverage/canopy area
|  |  | Vegetative Growth |  |  | 40
|  |  | Microgreens |  |  | 22.5
|  |  | Propagation |  |  | 15
|  |  | Cannabis - Flowering Stage |  |  | 68.8
| [WattsEE] |  |  |  |  | 36 | Y | W/sqft | Efficient wattage per square foot of coverage/canopy area
| [IFkWh] | HVAC Heating Type | Gas Heating |  |  | 0 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the reduction of waste heat rejected by the efficient lighting
|  |  | Electric Resistance Heating |  |  | 0.24
|  |  | Electric Heat Pump Heating |  |  | 0.1
| [CF] |  |  |  |  | 1 | N |  | Coincidence factor
| [WHFd] | HVAC Cooling Type | Cooling |  |  | 1.28 | N |  | Waste Heat Factor for Demand to account for cooling savings from efficient lighting in cooled buildings
|  |  | No Cooling |  |  | 1
| [IFTherms] | HVAC Heating Type | Gas Heating |  |  | 0.01 | N |  | Lighting-HVAC Integration Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the reduction of waste heat rejected by the efficient lighting
|  |  | Other Heating Type |  |  | 0
| [HeatDays] |  |  |  |  | 197 | N | days | Heat season days per year

## Grain Bin Fan Controls - Deemed
Grain Bin Fan Controls - Deemed
| Measure Code: | NR-AGE-GRAIN-V01-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
7
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
TBD
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [Default kWh Savings Based on Bin Size]
| Time of Sale Demand (ΔkW) | = 0
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Default kWh Savings Based on Bin Size] | Bin Diameter | 24 | Bin Eave Height | 20 | 215 | C | kWh | Default energy savings (kWh) based on bin size
[5 empty] | 30 | 430
[5 empty] | 35 | 430
[5 empty] | 40 | 430
[5 empty] | 45 | 860
[5 empty] | 50 | 1290
[5 empty] | 55 | 1720
[5 empty] | 60 | 2150
[5 empty] | 65 | 2580
[5 empty] | 70 | 3440
[5 empty] | 75 | 4300
[5 empty] | 80 | 5590
[5 empty] | 85 | 6880
[5 empty] | 90 | 8170
[5 empty] | 95 | 9892
[5 empty] | 100 | 11610
|  |  | 36 |  | 20 | 430
[5 empty] | 30 | 430
[5 empty] | 35 | 860
[5 empty] | 40 | 1290
[5 empty] | 45 | 1720
[5 empty] | 50 | 2580
[5 empty] | 55 | 3440
[5 empty] | 60 | 4730
[5 empty] | 65 | 6450
[5 empty] | 70 | 8170
[5 empty] | 75 | 9890
[5 empty] | 80 | 12470
[5 empty] | 85 | 15480
[5 empty] | 90 | 18490
[5 empty] | 95 | 21930
[5 empty] | 100 | 26230
|  |  | 42 |  | 20 | 430
[5 empty] | 30 | 860
[5 empty] | 35 | 1290
[5 empty] | 40 | 1720
[5 empty] | 45 | 2580
[5 empty] | 50 | 3440
[5 empty] | 55 | 4730
[5 empty] | 60 | 6450
[5 empty] | 65 | 8600
[5 empty] | 70 | 10750
[5 empty] | 75 | 13760
[5 empty] | 80 | 17200
[5 empty] | 85 | 20640
[5 empty] | 90 | 24940
[5 empty] | 95 | 30100
[5 empty] | 100 | 35690
|  |  | 48 |  | 20 | 430
[5 empty] | 30 | 860
[5 empty] | 35 | 1290
[5 empty] | 40 | 2150
[5 empty] | 45 | 3440
[5 empty] | 50 | 4730
[5 empty] | 55 | 6450
[5 empty] | 60 | 8600
[5 empty] | 65 | 11180
[5 empty] | 70 | 14190
[5 empty] | 75 | 18060
[5 empty] | 80 | 22360
[5 empty] | 85 | 27090
[5 empty] | 90 | 32680
[5 empty] | 95 | 39130
[5 empty] | 100 | 46440
|  |  | 54 |  | 20 | 430
[5 empty] | 30 | 1290
[5 empty] | 35 | 1720
[5 empty] | 40 | 3010
[5 empty] | 45 | 4300
[5 empty] | 50 | 6020
[5 empty] | 55 | 8170
[5 empty] | 60 | 10750
[5 empty] | 65 | 14190
[5 empty] | 70 | 18060
[5 empty] | 75 | 22790
[5 empty] | 80 | 27950
[5 empty] | 85 | 34400
[5 empty] | 90 | 41710
[5 empty] | 95 | 49450
[5 empty] | 100 | 58910
|  |  | 60 |  | 20 | 860
[5 empty] | 30 | 1720
[5 empty] | 35 | 2150
[5 empty] | 40 | 3440
[5 empty] | 45 | 5160
[5 empty] | 50 | 7310
[5 empty] | 55 | 9890
[5 empty] | 60 | 13330
[5 empty] | 65 | 17200
[5 empty] | 70 | 22360
[5 empty] | 75 | 27950
[5 empty] | 80 | 34830
[5 empty] | 85 | 42570
[5 empty] | 90 | 51170
[5 empty] | 95 | 61060
[5 empty] | 100 | 72670
|  |  | 72 |  | 20 | 860
[5 empty] | 30 | 2150
[5 empty] | 35 | 3440
[5 empty] | 40 | 5160
[5 empty] | 45 | 7310
[5 empty] | 50 | 10320
[5 empty] | 55 | 14190
[5 empty] | 60 | 19350
[5 empty] | 65 | 24940
[5 empty] | 70 | 32250
[5 empty] | 75 | 40420
[5 empty] | 80 | 49880
[5 empty] | 85 | 61060
[5 empty] | 90 | 73960
[5 empty] | 95 | 88150
[5 empty] | 100 | 104490
|  |  | 75 |  | 20 | 860
[5 empty] | 30 | 2150
[5 empty] | 35 | 3440
[5 empty] | 40 | 5590
[5 empty] | 45 | 8170
[5 empty] | 50 | 11180
[5 empty] | 55 | 15480
[5 empty] | 60 | 20640
[5 empty] | 65 | 27090
[5 empty] | 70 | 34830
[5 empty] | 75 | 43860
[5 empty] | 80 | 54180
[5 empty] | 85 | 66220
[5 empty] | 90 | 79980
[5 empty] | 95 | 95890
[5 empty] | 100 | 113090
|  |  | 78 |  | 20 | 1290
[5 empty] | 30 | 2580
[5 empty] | 35 | 3870
[5 empty] | 40 | 6020
[5 empty] | 45 | 8600
[5 empty] | 50 | 12470
[5 empty] | 55 | 16770
[5 empty] | 60 | 22360
[5 empty] | 65 | 29240
[5 empty] | 70 | 37840
[5 empty] | 75 | 47300
[5 empty] | 80 | 58910
[5 empty] | 85 | 71810
[5 empty] | 90 | 86860
[5 empty] | 95 | 103630
[5 empty] | 100 | 122550
|  |  | 90 |  | 20 | 1290
[5 empty] | 30 | 3440
[5 empty] | 35 | 5160
[5 empty] | 40 | 7740
[5 empty] | 45 | 11610
[5 empty] | 50 | 16340
[5 empty] | 55 | 22360
[5 empty] | 60 | 30100
[5 empty] | 65 | 39130
[5 empty] | 70 | 50310
[5 empty] | 75 | 63210
[5 empty] | 80 | 78260
[5 empty] | 85 | 95460
[5 empty] | 90 | 115240
[5 empty] | 95 | 138030
[5 empty] | 100 | 162970
|  |  | 105 |  | 20 | 2150
[5 empty] | 30 | 4730
[5 empty] | 35 | 7310
[5 empty] | 40 | 10750
[5 empty] | 45 | 15910
[5 empty] | 50 | 22360
[5 empty] | 55 | 30530
[5 empty] | 60 | 40850
[5 empty] | 65 | 53320
[5 empty] | 70 | 68370
[5 empty] | 75 | 86000
[5 empty] | 80 | 106210
[5 empty] | 85 | 29860
[5 empty] | 90 | 156950
[5 empty] | 95 | 187480
[5 empty] | 100 | 221880

## Grain Bin Fan Controls - Custom
Grain Bin Fan Controls - Custom
| Measure Code: | NR-AGE-GRAIN-V01-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
7
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
TBD
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [Fan_BHP] * [kWh Savings per Hp]
| Time of Sale Demand (ΔkW) | = 0
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [kWh Savings per Hp] |  |  | = ([0.746] * ([Hours_Manual] - [Hours_Control])) / [Eff_Motor]
| [Fan_BHP] |  |  | = ([Design CFM] * [Static Pressure]) / ([6356] * [Eff_Fan]) * (1 + [Exhaust Fan Factor])
| [Design CFM] |  |  | = [Bushel Capacity] * [CFM per Bushel]
| [Bushel Capacity] |  |  | = [π] * ([Diameter] / 2) * [Eave Height] * [Bushels per cubic foot]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [0.746] |  |  |  |  | 0.746 | N | kW/hp | Conversion factor from hp to kW
| [Hours_Manual] |  |  |  |  | 720 | Y | Hours | Annual hours of operation for grain storage bin aeration fans with manual controls
| [Hours_Control] |  |  |  |  | 180 | N | Hours | Annual hours of operation for grain storage bin aeration fans with controls
| [Eff_Motor] |  |  |  |  | 0.936 | Y |  | Efficiency of the fan motor
| [Static Pressure] | Grain Depth | 20 |  |  | 0.71 | C | in.wg | The design static pressure of the stored grain required to be overcome by the aeration fan. Value as determined from the following polynomial where x is the bin eave height in feet, assuming the default value for CFM per Bushel of 0.17. [= ax^2 + bx + c]
|  |  | 30 |  |  | 1.1
|  |  | 40 |  |  | 1.92
|  |  | 50 |  |  | 3.17
|  |  | 60 |  |  | 4.85
|  |  | 70 |  |  | 6.96
|  |  | 80 |  |  | 9.49
|  |  | 90 |  |  | 12.45
|  |  | 100 |  |  | 15.84
| [6356] |  |  |  |  | 6356 | N |  | Conversion factor from CFM to horsepower
| [Eff_Fan] |  |  |  |  | 0.6 | N |  | Efficiency of the fan
| [Exhaust Fan Factor] |  |  |  |  | 0.05 | N |  | Percentage of the aeration fan horsepower that can be attributed to the bin exhaust fans, which are also controlled in the system
| [CFM per Bushel] |  |  |  |  | 0.17 | N | CFM/bushel | CFM required per bushel for effective aeration
| [Diameter] | [5 empty] | Y | ft | Diameter of the storage bin, in feet
| [Eave Height] | [5 empty] | Y | ft | Height of the storage bin walls before the roof begins, not to be confused with peak height, which is the top of the roof
| [Bushels per cubic foot] |  |  |  |  | 0.804 | Y | Bushels/cubic foot | Bushels per cubic foot (for storage)

## Low Flow Faucet Aerators
Low Flow Faucet Aerators
| Measure Code: | NR-HWE-LFFA-V03-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
9
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known | Actual
|  | Unknown | 16
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [%ElectricDHW] * ([GPM_base] - [GPM_low]) / ([GPM_base]) * [Usage] * [EPG_electric] * [ISR]
| Time of Sale Demand (ΔkW) | = ([ΔkWh]) / [Hours] * [CF]
| Time of Sale Gas (ΔTherms) | = [%FossilDHW] * ([GPM_base] - [GPM_low]) / ([GPM_base]) * [Usage] * [EPG_gas] * [ISR]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [365.25]
| Time of Sale Water (ΔGallons) | = ([GPM_base] - [GPM_low]) / ([GPM_base]) * [Usage] * [ISR]
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [GPM_base] |  |  | = [Measured full throttle flow] * [0.83]
| [GPM_low] |  |  | =[Rated full throttle flow] * [0.95]
| [EPG_electric] |  |  | = ([γWater] * [1.0] * ([WaterTemp] - [SupplyTemp])) / ([RE_electric] * [3412])
| [Hours] |  |  | = ([Usage] * [0.479] )/ [GPH]
| [EPG_gas] |  |  | = ([8.33] * [1.0] * ([WaterTemp] - [SupplyTemp])) / ([RE_gas] * [100,000])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [%ElectricDHW] | Fuel Type | Electric |  |  | 100% | N |  | Proportion of water heating supplied by electric resistance heating
|  |  | Fossil Fuel |  |  | 0%
|  |  | Unknown |  |  | 53%
| [GPM_base] |  |  |  |  | 1.83 | C | GMP | Average flow rate, in gallons per minute, of the baseline faucet "as-used"
| [Measured full throttle flow] | [5 empty] | Y | GPM | Measured Full Throttle Flow of baseline faucet
| [0.83] | [5 empty] | N |  | Base faucet throttling factor
| [GPM_low] |  |  |  |  | 1.43 | C | GPM | Average flow rate, in gallons per minute, of the low-flow faucet aerator "as-used". Default when flow not measured assumes 1.5 GPM flow.
| [Rated full throttle flow] | [5 empty] | Y | GPM | Rated Full Throttle Flow of low-flow faucet
| [0.95] | [5 empty] | N |  | Low flow faucet throttling factor
| [Usage] | Building Type | Small Office |  |  | 2500 | Y | Gallons | Estimated usage of mixed water (mixture of hot water from water heater line and cold water line) per faucet
|  |  | Large Office |  |  | 11250
|  |  | Fast Food Rest. |  |  | 9588
|  |  | Sit-Down Rest. |  |  | 15779
|  |  | Retail |  |  | 3653
|  |  | Grocery |  |  | 3653
|  |  | Warehouse |  |  | 2500
|  |  | Elementary School |  |  | 3000
|  |  | Jr/Sr High School |  |  | 9000
|  |  | Health |  |  | 16436
|  |  | Motel |  |  | 1826
|  |  | Hotel |  |  | 1278
|  |  | Other |  |  | 5000
| [EPG_electric] | Water Heater Type | Resistane Tank or Unknown |  |  | 0.0822 | C | kWh/gal | Energy per gallon of mixed water used by faucet (electric water heater)
|  |  | Heat Pump Water Tank |  |  | 0.0403
| [γWater] |  |  |  |  | 8.33 | N | lbs/gal | Specific weight of water
| [1.0] |  |  |  |  | 1 | N | Btu/lb-°F | Heat Capacity of water
| [WaterTemp] | Location | Bath |  |  | 86 | N | °F | Assumed temperature of mixed water
|  |  | Kitchen |  |  | 93
| [SupplyTemp] |  |  |  |  | 56.5 | N | °F | Assumed temperature of water entering building
| [RE_electric] | Water Heater Type | Electric Resistance (or unknown) |  |  | 98% | N | Percentage | Recovery efficiency of electric water heater
|  |  | Heat Pump Water Heaters |  |  | 200%
| [3412] |  |  |  |  | 3412 | N | Btu/kWh | Converts Bto to kWh
| [ISR] |  |  |  |  | 1 | N |  | In service rate of faucet aerators
| [ΔkWh] | DHW Type | Resistance Tank | Building Type | Small Office | 44.9 | C | kWh | Calculated value above per faucet basis. Values based on all defaults provided.
[5 empty] | Large Office | 202.2
[5 empty] | Fast Food Rest. | 172.3
[5 empty] | Sit-Down Rest. | 283.5
[5 empty] | Retail | 65.6
[5 empty] | Grocery | 65.6
[5 empty] | Warehouse | 44.9
[5 empty] | Elementary School | 53.9
[5 empty] | Jr/Sr High School | 161.7
[5 empty] | Health | 295.3
[5 empty] | Motel | 32.8
[5 empty] | Hotel | 23
[5 empty] | Other | 89.8
|  |  | Heat Pump Tank | Building Type | Small Office | 22
[5 empty] | Large Office | 99.1
[5 empty] | Fast Food Rest. | 84.4
[5 empty] | Sit-Down Rest. | 138.8
[5 empty] | Retail | 32.1
[5 empty] | Grocery | 32.1
[5 empty] | Warehouse | 22
[5 empty] | Elementary School | 26.4
[5 empty] | Jr/Sr High School | 79.2
[5 empty] | Health | 144.6
[5 empty] | Motel | 16.1
[5 empty] | Hotel | 11.2
[5 empty] | Other | 44
|  |  | Unknown DHW | Building Type | Small Office | 23.8
[5 empty] | Large Office | 107.1
[5 empty] | Fast Food Rest. | 91.3
[5 empty] | Sit-Down Rest. | 150.3
[5 empty] | Retail | 34.8
[5 empty] | Grocery | 34.8
[5 empty] | Warehouse | 23.8
[5 empty] | Elementary School | 28.6
[5 empty] | Jr/Sr High School | 85.7
[5 empty] | Health | 156.5
[5 empty] | Motel | 17.4
[5 empty] | Hotel | 12.2
[5 empty] | Other | 47.6
| [Hours] | Building Type | Small Office | Tank Type | Resistance | 17.4 | C | Hours | Annual electric DHW recovery hours for faucet use. Values based on defaults above.
|  |  | Large Office |  |  | 78.3
|  |  | Fast Food Rest. |  |  | 66.7
|  |  | Sit-Down Rest. |  |  | 109.8
|  |  | Retail |  |  | 25.4
|  |  | Grocery |  |  | 25.4
|  |  | Warehouse |  |  | 17.4
|  |  | Elementary School |  |  | 20.9
|  |  | Jr/Sr High School |  |  | 62.7
|  |  | Health |  |  | 114.4
|  |  | Motel |  |  | 12.7
|  |  | Hotel |  |  | 8.9
|  |  | Other |  |  | 34.8
|  |  | Small Office |  | Heat Pump | 8.5
|  |  | Large Office |  |  | 38.4
|  |  | Fast Food Rest. |  |  | 32.7
|  |  | Sit-Down Rest. |  |  | 53.8
|  |  | Retail |  |  | 12.5
|  |  | Grocery |  |  | 12.5
|  |  | Warehouse |  |  | 8.5
|  |  | Elementary School |  |  | 10.2
|  |  | Jr/Sr High School |  |  | 30.7
|  |  | Health |  |  | 56
|  |  | Motel |  |  | 6.2
|  |  | Hotel |  |  | 4.4
|  |  | Other |  |  | 17.1
| [GPH] | Water Heater Type | Resistance |  |  | 68.8 | N | gal/hour | Gallons per hour recovery of electric water heater calculated for 70F temp rise (126.5-56.5), 98% for resistance (or unknown) or 200% for heat pump water tanks recovery efficiency, and typical 12kW electric resistance storage tank
|  |  | Heat Pump |  |  | 140.4
| [CF] | Building Type | Small Office | Tank Type | Resistance | 0.0045 | N |  | Coincidence Factor for electric load reduction
|  |  | Large Office |  |  | 0.0238
|  |  | Fast Food Rest. |  |  | 0.0114
|  |  | Sit-Down Rest. |  |  | 0.025
|  |  | Retail |  |  | 0.0058
|  |  | Grocery |  |  | 0.0058
|  |  | Warehouse |  |  | 0.006
|  |  | Elementary School |  |  | 0.0054
|  |  | Jr/Sr High School |  |  | 0.0161
|  |  | Health |  |  | 0.0196
|  |  | Motel |  |  | 0.0009
|  |  | Hotel |  |  | 0.0006
|  |  | Other |  |  | 0.0119
|  |  | Small Office |  | Heat Pump | 0.0016
|  |  | Large Office |  |  | 0.0083
|  |  | Fast Food Rest. |  |  | 0.004
|  |  | Sit-Down Rest. |  |  | 0.0088
|  |  | Retail |  |  | 0.002
|  |  | Grocery |  |  | 0.002
|  |  | Warehouse |  |  | 0.00211
|  |  | Elementary School |  |  | 0.0019
|  |  | Jr/Sr High School |  |  | 0.0056
|  |  | Health |  |  | 0.0069
|  |  | Motel |  |  | 0.0003
|  |  | Hotel |  |  | 0.0002
|  |  | Other |  |  | 0.0042
| [ΔkW] | DHW Type | Resistance Tank | Building Type | Small Office | 0.0115 | C | kW | Calculated value above per faucet basis. Values based on all defaults provided.
[5 empty] | Large Office | 0.0615
[5 empty] | Fast Food Rest. | 0.0295
[5 empty] | Sit-Down Rest. | 0.0647
[5 empty] | Retail | 0.015
[5 empty] | Grocery | 0.015
[5 empty] | Warehouse | 0.0154
[5 empty] | Elementary School | 0.0138
[5 empty] | Jr/Sr High School | 0.0415
[5 empty] | Health | 0.0505
[5 empty] | Motel | 0.0022
[5 empty] | Hotel | 0.0016
[5 empty] | Other | 0.0308
|  |  | Heat Pump Tank | Building Type | Small Office | 0.0057
[5 empty] | Large Office | 0.0302
[5 empty] | Fast Food Rest. | 0.0144
[5 empty] | Sit-Down Rest. | 0.0317
[5 empty] | Retail | 0.0073
[5 empty] | Grocery | 0.0073
[5 empty] | Warehouse | 0.0075
[5 empty] | Elementary School | 0.0068
[5 empty] | Jr/Sr High School | 0.0204
[5 empty] | Health | 0.0248
[5 empty] | Motel | 0.0011
[5 empty] | Hotel | 0.0008
[5 empty] | Other | 0.0151
|  |  | Unknown DHW | Building Type | Small Office | 0.0061
[5 empty] | Large Office | 0.0326
[5 empty] | Fast Food Rest. | 0.0156
[5 empty] | Sit-Down Rest. | 0.0343
[5 empty] | Retail | 0.0079
[5 empty] | Grocery | 0.0079
[5 empty] | Warehouse | 0.0082
[5 empty] | Elementary School | 0.0073
[5 empty] | Jr/Sr High School | 0.022
[5 empty] | Health | 0.0268
[5 empty] | Motel | 0.0012
[5 empty] | Hotel | 0.0008
[5 empty] | Other | 0.0163
| [%FossilDHW] | Fuel Type | Electric |  |  | 0% | N |  | Proportion of water heating supplied by fossil fuel heating
|  |  | Fossil Fuel |  |  | 100%
|  |  | Unknown |  |  | 47%
| [EPG_gas] | Tank Type | Storage Tank |  |  | 0.0035 | C |  | Energy per gallon of mixed water used by faucet (gas water heater)
|  |  | Centrail Boiler |  |  | 0.0047
|  |  | Unknown |  |  | 0.004
| [RE_gas] | Tank Type | Storage Tank |  |  | 78% | N |  | Recovery efficiency of gas water heater
|  |  | Centrail Boiler |  |  | 59%
|  |  | Unknown |  |  | 69%
| [100,000] |  |  |  |  | 100000 | N | Btu/Therm | Converts Btus to Therms
| [ΔTherms] | DHW Type | Storage Tank | Building Type | Small Office | 1.9 | C | Therm | Calculated value above per faucet basis. Values based on all defaults provided.
[5 empty] | Large Office | 8.7
[5 empty] | Fast Food Rest. | 7.4
[5 empty] | Sit-Down Rest. | 12.2
[5 empty] | Retail | 2.8
[5 empty] | Grocery | 2.8
[5 empty] | Warehouse | 1.9
[5 empty] | Elementary School | 2.3
[5 empty] | Jr/Sr High School | 6.9
[5 empty] | Health | 12.7
[5 empty] | Motel | 1.4
[5 empty] | Hotel | 1
[5 empty] | Other | 3.9
|  |  | Central Boiler DHW | Building Type | Small Office | 2.5
[5 empty] | Large Office | 11.5
[5 empty] | Fast Food Rest. | 9.8
[5 empty] | Sit-Down Rest. | 16.1
[5 empty] | Retail | 3.7
[5 empty] | Grocery | 3.7
[5 empty] | Warehouse | 2.5
[5 empty] | Elementary School | 3.1
[5 empty] | Jr/Sr High School | 9.2
[5 empty] | Health | 16.7
[5 empty] | Motel | 1.9
[5 empty] | Hotel | 1.3
[5 empty] | Other | 5.1
|  |  | Unknown Gas DHW | Building Type | Small Office | 2.2
[5 empty] | Large Office | 9.8
[5 empty] | Fast Food Rest. | 8.3
[5 empty] | Sit-Down Rest. | 13.7
[5 empty] | Retail | 3.2
[5 empty] | Grocery | 3.2
[5 empty] | Warehouse | 2.2
[5 empty] | Elementary School | 2.6
[5 empty] | Jr/Sr High School | 7.8
[5 empty] | Health | 14.3
[5 empty] | Motel | 1.6
[5 empty] | Hotel | 1.1
[5 empty] | Other | 4.4
|  |  | Unknown DHW | Building Type | Small Office | 1
[5 empty] | Large Office | 4.6
[5 empty] | Fast Food Rest. | 3.9
[5 empty] | Sit-Down Rest. | 6.5
[5 empty] | Retail | 1.5
[5 empty] | Grocery | 1.5
[5 empty] | Warehouse | 1
[5 empty] | Elementary School | 1.2
[5 empty] | Jr/Sr High School | 3.7
[5 empty] | Health | 6.7
[5 empty] | Motel | 0.7
[5 empty] | Hotel | 0.5
[5 empty] | Other | 2
| [365.25] |  |  |  |  | 365.25 | N | Days | Days per year
| [ΔPeakTherms] | DHW Type | Storage Tank | Building Type | Small Office | 0.0053 | C | Therm | Calculated value above per faucet basis. Values based on all defaults provided.
[5 empty] | Large Office | 0.0237
[5 empty] | Fast Food Rest. | 0.0202
[5 empty] | Sit-Down Rest. | 0.0333
[5 empty] | Retail | 0.0077
[5 empty] | Grocery | 0.0077
[5 empty] | Warehouse | 0.0053
[5 empty] | Elementary School | 0.0063
[5 empty] | Jr/Sr High School | 0.019
[5 empty] | Health | 0.0346
[5 empty] | Motel | 0.0038
[5 empty] | Hotel | 0.0027
[5 empty] | Other | 0.0105
|  |  | Central Boiler DHW | Building Type | Small Office | 0.007
[5 empty] | Large Office | 0.0314
[5 empty] | Fast Food Rest. | 0.0267
[5 empty] | Sit-Down Rest. | 0.044
[5 empty] | Retail | 0.0102
[5 empty] | Grocery | 0.0102
[5 empty] | Warehouse | 0.007
[5 empty] | Elementary School | 0.0084
[5 empty] | Jr/Sr High School | 0.0251
[5 empty] | Health | 0.0458
[5 empty] | Motel | 0.0051
[5 empty] | Hotel | 0.0036
[5 empty] | Other | 0.0139
|  |  | Unknown Gas DHW | Building Type | Small Office | 0.006
[5 empty] | Large Office | 0.0268
[5 empty] | Fast Food Rest. | 0.0228
[5 empty] | Sit-Down Rest. | 0.0376
[5 empty] | Retail | 0.0087
[5 empty] | Grocery | 0.0087
[5 empty] | Warehouse | 0.006
[5 empty] | Elementary School | 0.0072
[5 empty] | Jr/Sr High School | 0.0215
[5 empty] | Health | 0.0392
[5 empty] | Motel | 0.0044
[5 empty] | Hotel | 0.003
[5 empty] | Other | 0.0119
|  |  | Unknown DHW | Building Type | Small Office | 0.0028
[5 empty] | Large Office | 0.0126
[5 empty] | Fast Food Rest. | 0.0107
[5 empty] | Sit-Down Rest. | 0.0177
[5 empty] | Retail | 0.0041
[5 empty] | Grocery | 0.0041
[5 empty] | Warehouse | 0.0028
[5 empty] | Elementary School | 0.0034
[5 empty] | Jr/Sr High School | 0.0101
[5 empty] | Health | 0.0184
[5 empty] | Motel | 0.002
[5 empty] | Hotel | 0.0014
[5 empty] | Other | 0.0056
| [ΔGallons] | Building Type | Small Office |  |  | 546 | C | Gallons | Calculated value above per faucet basis. Values based on all defaults provided.
|  |  | Large Office |  |  | 2459
|  |  | Fast Food Rest. |  |  | 2094
|  |  | Sit-Down Rest. |  |  | 3447
|  |  | Retail |  |  | 798
|  |  | Grocery |  |  | 798
|  |  | Warehouse |  |  | 546
|  |  | Elementary School |  |  | 656
|  |  | Jr/Sr High School |  |  | 1967
|  |  | Health |  |  | 3590
|  |  | Motel |  |  | 399
|  |  | Hotel |  |  | 279
|  |  | Other |  |  | 1093

## Low Flow Showerheads
Low Flow Showerheads
| Measure Code: | NR-HWE-LFSH-V04-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
10
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known | Actual
|  | Unknown | 20
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [%ElectricDHW] * (([GPM_base] - [GPM_low]) * [L * SPD * Days] ) * [EPG_electric] * [ISR]
| Time of Sale Demand (ΔkW) | = [ΔkWh] / [Hours] * [CF]
| Time of Sale Gas (ΔTherms) | = [%FossilDHW] * ([GPM_base] - [GPM_low]) * [L * SPD * Days] * [EPG_gas] * [ISR]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [365.25]
| Time of Sale Water (ΔGallons) | = ([GPM_base] - [GPM_low] ) *[L * SPD * Days] * [ISR]
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [(L * SPD * Days)] |  |  | =[(L * SPD * Days)]
| [EPG_electric] |  |  | = ([γWater] * [1.0] * ([ShowerTemp] - [SupplyTemp])) / ([RE_electric] * [3412])
| [Hours] |  |  | = ([GPM_base] *[L] * [SPD] * [365.25] * [0.65] )/ [GPH]
| [EPG_gas] |  |  | = ([8.33] * [1.0] * ([ShowerTemp] - [SupplyTemp])) / ([RE_gas] * [100,000])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [%ElectricDHW] | Fuel Type | Electric |  |  | 100% | N |  | Proportion of water heating supplied by electric resistance heating
|  |  | Fossil Fuel |  |  | 0%
|  |  | Unknown |  |  | 53%
| [GPM_base] |  |  |  |  | 2.5 | Y | GPM | Flow rate of the baseline showerhead
| [GPM_low] |  |  |  |  | 1.5 | Y | GPM | Flow rate of the low-flow showerhead
| [(L * SPD * Days)] | Building Type | Hospitality |  |  | 3509 | C | Minutes | Minutes of use per showerhead annually. Ideally apply the custom calculation. If not possible use defaults provided.
|  |  | Health |  |  | 2528
|  |  | Commercial – Employee Shower |  |  | 1894
|  |  | Education |  |  | 2057
|  |  | Other Commercial Except Fitness Center |  |  | 3029
|  |  | Fitness Center |  |  | 56893
| [L] |  |  |  |  | 7.8 | Y | Minutes | Shower length in minutes with showerhead
| [SPD] | [5 empty] | Y |  | Showers Per Day for showerhead
| [Days] | [5 empty] | Y | days | Days per year, on average
| [EPG_electric] | Water Heater Type | Resistance or unknown |  |  | 0.1109 | C |  | Energy per gallon of hot water supplied by electric
|  |  | Heat Pump |  |  | 0.0543
| [γWater] |  |  |  |  | 8.33 | N | lbs/gal | Specific weight of water
| [1.0] |  |  |  |  | 1 | N | Btu/lb-°F | Heat Capacity of water
| [ShowerTemp] |  |  |  |  | 101 | N | °F | Assumed temperature of water
| [SupplyTemp] |  |  |  |  | 56.5 | N | °F | Assuned tenperature of water entering house
| [RE_electric] | Water Heater Type | Electric Resistance (or unknown) |  |  | 98% | N |  | Average recovery efficiency of electric water heater
|  |  | Heat Pump Water Heaters |  |  | 200%
| [3412] |  |  |  |  | 3412 | N | Btu/kWh | Converts Bto to kWh
| [ISR] |  |  |  |  | 1 | N |  | In service rate of showerheads
| [ΔkWh] | [5 empty] | C | kWh | calculated value above per faucet basis
| [Hours] | [5 empty] | C | Hours | Annual electric DHW recovery hours for showerhead use
| [GPH] | Water Heater Type | Resistance |  |  | 68.8 | N | gal/hour | Gallons per hour recovery of electric water heater calculated for 70F temp rise (126.5-56.5), 98% recovery efficiency for electric resistance (or unknown) and 200% for heat pump water heaters, and typical 12kW electric resistance storage tank
|  |  | Heat Pump |  |  | 140.4
| [CF] |  |  |  |  | 1.6% | N |  | Coincidence Factor for electric load reduction
| [%FossilDHW] | Fuel Type | Electric |  |  | 0% | N |  | Proportion of water heating supplied by fossil fuel heating
|  |  | Fossil Fuel |  |  | 100%
|  |  | Unknown |  |  | 47%
| [EPG_gas] | Tank Type | Storage Tank |  |  | 0.0048 | C |  | Energy per gallon of Hot water supplied by gas
|  |  | Centrail Boiler |  |  | 0.0063
|  |  | Unknown |  |  | 0.0054
| [RE_gas] | Tank Type | Storage Tank |  |  | 78% | N |  | Recovery efficiency of gas water heater
|  |  | Centrail Boiler |  |  | 59%
|  |  | Unknown |  |  | 69%
| [100,000] |  |  |  |  | 100000 | N | Btu/Therm | Converts Btus to Therms
| [ΔTherms] | [5 empty] | C | therm | Therm impact calculated above
| [365.25] |  |  |  |  | 365.25 | N | Days | Days per year

## Gas Hot Water Heater
Gas Hot Water Heater
| Measure Code: | NR-HWE-GHWH-V05-210101
| Lifetime of Efficient Equipment: | [8 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime | [6 empty] | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
| Water Heater Type | Storage Tank | 15
|  | Tankless | 20
| Measure Cost: | [8 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Incremental Install Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known |  |  |  |  | Actual | Actual
|  | Unknown | Equipment Type | Gas Storage Water Heaters ≤ 75,000 Btu/h, ≤55 Gallons | Category | Baseline | N/A | 616
[6 empty] | Efficient | 440 | 1055
|  |  |  | Gas Storage Water Heaters > 75,000 Btu/h |  | 0.80 Et | N/A | 4886
[6 empty] | 0.83 Et | 220 | 5106
[6 empty] | 0.84 Et | 413 | 5299
[6 empty] | 0.85 Et | 529 | 5415
[6 empty] | 0.86 Et | 646 | 5532
[6 empty] | 0.87 Et | 762 | 5648
[6 empty] | 0.88 Et | 879 | 5765
[6 empty] | 0.89 Et | 996 | 5882
[6 empty] | 0.90 Et | 1135 | 6021
|  |  |  | Gas Tankless Water Heaters >50,000 Btu/h and <200,000 Btu/h |  | Tankless Baseline | N/A | 593
[6 empty] | Efficient | 487 | 1080
[6 empty] | Incremental using Storage Baseline | 465
|  |  |  | Gas Tankless Water Heaters ≥200,000 Btu/h |  | Tankless Baseline | N/A | 1148
[6 empty] | Efficient | 278 | 1427
[6 empty] | Incremental using Storage Baseline | -3459
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
| Tank type | Gas fired tankless | 1 | 100
|  | All other | N/A | N/A
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | = [∆Therms_Unit] + [∆Therms_Standby]
| Time of Sale Peak Gas (ΔPeakTherms) | = ([ΔTherms] ) / [365.25]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Sub Algorithm
| [∆Therms_Unit] |  |  |  |  | = (([T_out] - [T_in] ) * [HotWaterUse_Gallon] * [γWater] * [1 ] * (1/ [µ_base] - 1/[µ_Eff ]) / [100,000])
| [HotWaterUseGallon] | Method of estimation | Actual |  |  | Actual
|  |  | Water Heater Capacity |  |  | = [Capacity] * [Consumption/cap]
|  |  | Facility Size |  |  | = [Area]/1000 * [Consumption/1000 sq. ft.]
| [µbase] | Equipment Type | Residential-duty Gas Storage ≤ 125,000 Btu/h | Draw Pattern | Very small | UEF = 0.2674 – (0.0009 * [Rated Storage Volume])
[5 empty] | Low | UEF = 0.5362 – (0.0012 * [Rated Storage Volume])
[5 empty] | Medium | UEF = 0.6002 – (0.0011 * [Rated Storage Volume])
[5 empty] | High | UEF = 0.6597 – (0.0009 * [Rated Storage Volume])
|  |  | Residential Gas Instantaneous Water Heaters ≤ 200,000 Btu/h |  | Very low | UEF = 0.80
[5 empty] | All other | UEF = 0.81
|  |  | Commercial Gas Storage > 75,000 Btu/h |  | All | Ethermal = 80%
|  |  | Commercial Gas Tankless > 200,000 Btu/h |  | All | Ethermal = 80%
| [∆Therms_Standby] | Water heater type and size | Commercial Gas Storage >75,000 Btu/h |  |  | =([SL_base] - [SL_eff]) * [8766]) / [100,000]
|  |  | All other |  |  | 0
| [SLbase] |  |  |  |  | = [Q]/800 + 110√[Rated Storage Volume]
| [SLeff] |  |  |  |  | = [Q]/800 + 110√[Rated Storage Volume]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Tout] |  |  |  |  | 140 | Y | °F | Unmixed Outlet Water Temperature
| [Tin] |  |  |  |  | 56.5 | Y | °F | Inlet Water Temperature
| [HotWaterUseGallon] | [5 empty] | C | Gallons | Estimated annual hot water consumption
| [Consumption/cap] | Building Type | Convenience |  |  | 528 | N | Gallons | Estimate of consumption per gallon of usable tank capacity, dependent on building type
|  |  | Education |  |  | 568
|  |  | Grocery |  |  | 528
|  |  | Health |  |  | 788
|  |  | Large Office |  |  | 511
|  |  | Large Retail |  |  | 528
|  |  | Lodging |  |  | 715
|  |  | Other Commercial |  |  | 341
|  |  | Restaurant |  |  | 377
|  |  | Small Office |  |  | 511
|  |  | Small Retail |  |  | 528
|  |  | Warehouse |  |  | 341
|  |  | Nursing |  |  | 672
|  |  | Multifamily |  |  | 894
| [Capacity] | [5 empty] | Y |  | Usable capacity of hot water storage tank in gallons
| [Area] | [5 empty] | Y |  | Area in sq. ft. that is served by DHW boiler
| [Consumption/1000 sq. ft.] | Building Type | Convenience |  |  | 3634 | N | Gallons | Estimate of DHW consumption (gallons) per 1000 ft2 of floor area
|  |  | Education |  |  | 5440
|  |  | Grocery |  |  | 1150
|  |  | Health |  |  | 13663
|  |  | Large Office |  |  | 1205
|  |  | Large Retail |  |  | 157
|  |  | Lodging |  |  | 18541
|  |  | Other Commercial |  |  | 3573
|  |  | Restaurant |  |  | 26927
|  |  | Small Office |  |  | 931
|  |  | Small Retail |  |  | 913
|  |  | Warehouse |  |  | 476
|  |  | Nursing |  |  | 26721
|  |  | Multifamily |  |  | 13133
| [γWater] |  |  |  |  | 8.33 | N | lbs/gal | Specific weight of water
| [1] |  |  |  |  | 1 | N | Btu/lbm/°F | Specific heat of water
| [µbase] | [5 empty] | C |  | Rated efficiency of baseline water heater
| [µeff] | [5 empty] | Y |  | Rated efficiency of efficient water heater
| [100,000] |  |  |  |  | 100000 | N | Btu/Therm | Converts Btus to Therms
| [∆Therms_Standby] | [5 empty] | C |  | Additional savings due to lower standby losses
| [SLbase] | [5 empty] | C |  | Standby loss of baseline unit
| [Q] | [5 empty] | Y | Btu/h | Nameplate input rating in Btu/h
| [Rated Storage Volume] | [5 empty] | Y | Gallons | Rated volume in gallons
| [SLeff] | [5 empty] | Y | Btu/h | Nameplate standy loss of new water rheater in Btu/h
| [8766] | [5 empty] | N | Hours | Hours per year
| [ΔTherms] | [5 empty] | C | therm | Therm impact calculated above
| [365.25] |  |  |  |  | 365.25 | N | Days | Days per year

## Controls Cent. Dom. Hot Water
Controls Cent. Dom. Hot Water
| Measure Code: | NR-HWE-DHWC-V02-180101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known |  | Actual
|  | Unknown |  | 1200
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = 651kWh
| Time of Sale Demand (ΔkW) | = 0
| Time of Sale Gas (ΔTherms) | = [55.9] * [number of dwelling units]
| Time of Sale Peak Gas (ΔPeakTherms) | = ([ΔTherms ]) / [365.25]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [kWh] |  |  |  |  | 651 | N | kWh | Deemed savings
| [∆Therms] | [5 empty] | C | Therms | Therm impact calculated above
| [55.9] |  |  |  |  | 55.9 | N | Therms | Deemed Therm savings per unit
| [number of dwelling units] | [5 empty] | Y |  | Number of dwelling units
| [365.25] |  |  |  |  | 365.25 | N | Days | Days per year

## Pool Covers
Pool Covers
| Measure Code: | NR-HWE-PCOV-V02-180101
| Lifetime of Efficient Equipment: | [6 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
6
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known |  |  |  | Actual
|  | Unknown | Control type | Manually operated |  | $1.5 / sqft
|  |  |  | Automatic |  | $6.5 / sqft
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | =(∑Season([Savings Factor] * [Sqft]) / [η_heat ]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms ] / [Days]
| Time of Sale Water (ΔGallons) | =([Sqft] * [h_makeup] * [Freq] * [7.48052] * [0.3]) / [12]
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Savings Factor] | Season and Location | Spring |  |  | 0.37 | N | Therms / ft2 | Dependent on season and location
|  |  | Summer |  |  | 0.21
|  |  | Fall |  |  | 0.77
|  |  | Winter |  |  | 0.92
|  |  | Year-round |  |  | 2.27
|  |  | Indoor |  |  | 0.9
| [Sqft] | [5 empty] | Y | ft2 | Surface area of the pool
| [ηheat] | [5 empty] | Y |  | Efficiency of gas heating system
| [∆Therms] | [5 empty] | C | Therms | Therm impact calculated above
| [Days] | [5 empty] | Y | Days | Days in operating season
| [hmakeup] | [5 empty] | Y | Inches | Height, in inches, the pool is typically filled when make-up water is added
| [Freq] | [5 empty] | Y |  | Total number of water make-up events throughout the operating season
| [7.48052] |  |  |  |  | 7.48052 | N | Gallons/ft3 | Gallons of water per ft3
| [12] |  |  |  |  | 12 | N | inches/ft | Inches per foot
| [0.3] | [5 empty] | N |  | Conservative estimate for the reduction of make-up water required

## Drainwater Heat Recovery
Drainwater Heat Recovery
| Measure Code: | NR-HWE-DWHR-V03-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
25
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =(([T_out] - [T_in] ) * [HotWaterUse_Gallon]* [γWater] * [1] * [η_PRA]) / ([3,412] * [RE_electric])
| Time of Sale Demand (ΔkW) | = [∆kWh] / [Hours] * [CF]
| Time of Sale Gas (ΔTherms) | =(([T_out] - [T_in] ) * [HotWaterUse_Gallon] * [γWater] * [1] * [η_PRA]) / ([100,000] * [RE_gas])
| Time of Sale Peak Gas (ΔPeakTherms) | = ([Δtherms]) / [365.25]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [HotWaterUseGallon] | Method of estimation | Actual | Actual
|  |  | Water Heater Capacity | = [Capacity] * [Consumption/cap]
|  |  | Facility Size | = [Area/1000] * [Consumption/1000 sq. ft.]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Tout] |  |  |  |  | 140 | Y | °F | Unmixed Outlet Water Temperature from the DHW system
| [Tin] |  |  |  |  | 56.5 | Y | °F | Inlet Water Temperature to the DHW system
| [HotWaterUseGallon] | [5 empty] | C | Gallons | Estimated annual hot water consumption (gallons)
| [Consumption/cap] | Building Type | Convenience |  |  | 528 | N | Gallons | Estimate of consumption per gallon of usable tank capacity, dependent on building type
|  |  | Education |  |  | 568
|  |  | Grocery |  |  | 528
|  |  | Health |  |  | 788
|  |  | Large Office |  |  | 511
|  |  | Large Retail |  |  | 528
|  |  | Lodging |  |  | 715
|  |  | Other Commercial |  |  | 341
|  |  | Restaurant |  |  | 377
|  |  | Small Office |  |  | 511
|  |  | Small Retail |  |  | 528
|  |  | Warehouse |  |  | 341
|  |  | Nursing |  |  | 672
|  |  | Multifamily |  |  | 894
| [Capacity] | [5 empty] | Y |  | Usable capacity of hot water storage tank in gallons
| [Area] | [5 empty] | Y |  | Area in sq. ft. that is served by DHW boiler
| [Consumption/1000 sq. ft.] | Building Type | Convenience |  |  | 3634 | N | Gallons | Estimate of DHW consumption (gallons) per 1000 ft2 of floor area
|  |  | Education |  |  | 5440
|  |  | Grocery |  |  | 1150
|  |  | Health |  |  | 13663
|  |  | Large Office |  |  | 1205
|  |  | Large Retail |  |  | 157
|  |  | Lodging |  |  | 18541
|  |  | Other Commercial |  |  | 3573
|  |  | Restaurant |  |  | 26927
|  |  | Small Office |  |  | 931
|  |  | Small Retail |  |  | 913
|  |  | Warehouse |  |  | 476
|  |  | Nursing |  |  | 26721
|  |  | Multifamily |  |  | 13133
| [γWater] |  |  |  |  | 8.33 | N | lbs/gal | Specific weight capacity of water
| [1] |  |  |  |  | 1 | N | Btu/lbm/°F | Specific heat of water
| [ηPRA] |  |  |  |  | 25% | N |  | Practical effectiveness of drainwater heat recovery (percentage of DHW output energy that the device can recover)
| [3,412] |  |  |  |  | 3412 | N | Btu to kWh | Conversion from Btu to kWh
| [REelectric] |  |  |  |  | 0.98 | Y |  | Recovery efficiency of electric DHW system
| [Hours] |  |  |  |  | 8766 | N | Hours | Hours
| [CF] |  |  |  |  | 1 | N |  | Summer Peak Coincidence Factor
| [100,000] |  |  |  |  | 100000 | N | Btu to Therms | Converts Btu to Therms
| [REgas] |  |  |  |  | 78% | Y |  | Recovery efficiency of gas DHW system
| [∆Therms] | [5 empty] | C | Therms | Therm impact calculated above
| [365.25] |  |  |  |  | 365.25 | N | Days | Days per year

## Boiler
Boiler
| Measure Code: | NR-HVC-BOIL-V04-210101
| Lifetime of Efficient Equipment: | [6 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
25
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known |  |  | Actual - baseline | Actual
|  | Unknown | AFUE | 84% | N/A | 4053
|  |  |  | 85% | 415 | 4468
|  |  |  | 86% | 1211 | 5264
|  |  |  | 87% | 1223 | 5276
|  |  |  | 88% | 1344 | 5397
|  |  |  | 89% | 1465 | 5518
|  |  |  | 90% | 1585 | 5638
|  |  |  | 91% | 1530 | 5583
|  |  |  | 92% | 1681 | 5734
|  |  |  | 93% | 1832 | 5885
|  |  |  | 94% | 1983 | 6036
|  |  |  | 95% | 2135 | 6188
|  |  |  | 96% | 2286 | 6339
|  |  |  | 97% | 2437 | 6490
|  |  |  | 98% | 2588 | 6641
|  |  |  | 99% | 2739 | 6792
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | =([EFLH] * [Capacity] * (([EfficiencyRating (EE)]) / [EfficiencyRating(BASE)] -1)) / [100,000]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [EFLH] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1298 | N | Hours | Equivalent Full Load Hours for heating space
[5 empty] | Grocery |  |  | 1493
[5 empty] | Health |  |  | 1206
[5 empty] | Hospital |  |  | 1084
[5 empty] | Lodging |  |  | 1365
[5 empty] | Multifamily |  |  | 1521
[5 empty] | Office - Large |  |  | 1457
[5 empty] | Office - Small |  |  | 1250
[5 empty] | Restaurant |  |  | 1040
[5 empty] | Retail - Large |  |  | 1255
[5 empty] | Retail - Small |  |  | 1172
[5 empty] | Warehouse |  |  | 1277
[5 empty] | Convenience |  |  | 785
[5 empty] | Industrial |  |  | 849
[5 empty] | Religious |  |  | 1322
[5 empty] | Nonresidential Average |  |  | 1251
[5 empty] | Education |  | Zone 6 (Mason City) | 1529
[5 empty] | Grocery |  |  | 1754
[5 empty] | Health |  |  | 1430
[5 empty] | Hospital |  |  | 940
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1846
[5 empty] | Office - Large |  |  | 1748
[5 empty] | Office - Small |  |  | 1435
[5 empty] | Restaurant |  |  | 1324
[5 empty] | Retail - Large |  |  | 1523
[5 empty] | Retail - Small |  |  | 1471
[5 empty] | Warehouse |  |  | 1589
[5 empty] | Convenience |  |  | 1224
[5 empty] | Industrial |  |  | 1275
[5 empty] | Religious |  |  | 1873
[5 empty] | Nonresidential Average |  |  | 1555
[5 empty] | Education |  | Average/Unknown | 1351
[5 empty] | Grocery |  |  | 1601
[5 empty] | Health |  |  | 1346
[5 empty] | Hospital |  |  | 1082
[5 empty] | Lodging |  |  | 1494
[5 empty] | Multifamily |  |  | 1694
[5 empty] | Office - Large |  |  | 1549
[5 empty] | Office - Small |  |  | 1358
[5 empty] | Restaurant |  |  | 1173
[5 empty] | Retail - Large |  |  | 1348
[5 empty] | Retail - Small |  |  | 1372
[5 empty] | Warehouse |  |  | 1443
[5 empty] | Convenience |  |  | 1071
[5 empty] | Industrial |  |  | 1183
[5 empty] | Religious |  |  | 1796
[5 empty] | Nonresidential Average |  |  | 1438
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 510
[5 empty] | Health |  |  | 778
[5 empty] | Hospital |  |  | 1799
[5 empty] | Lodging |  |  | 1080
[5 empty] | Office - Large |  |  | 710
[5 empty] | Office - Small |  |  | 450
[5 empty] | Restaurant |  |  | 896
[5 empty] | Retail - Large |  |  | 709
[5 empty] | Retail - Small |  |  | 785
[5 empty] | Warehouse |  |  | 886
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 690
[5 empty] | Education |  | Zone 6 (Mason City) | 683
[5 empty] | Health |  |  | 972
[5 empty] | Hospital |  |  | 1520
[5 empty] | Lodging |  |  | 1491
[5 empty] | Office - Large |  |  | 917
[5 empty] | Office - Small |  |  | 590
[5 empty] | Restaurant |  |  | 1192
[5 empty] | Retail - Large |  |  | 906
[5 empty] | Retail - Small |  |  | 1036
[5 empty] | Warehouse |  |  | 1238
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 930
[5 empty] | Education |  | Average/Unknown | 591
[5 empty] | Health |  |  | 864
[5 empty] | Hospital |  |  | 2196
[5 empty] | Lodging |  |  | 1471
[5 empty] | Office - Large |  |  | 862
[5 empty] | Office - Small |  |  | 492
[5 empty] | Restaurant |  |  | 1048
[5 empty] | Retail - Large |  |  | 839
[5 empty] | Retail - Small |  |  | 986
[5 empty] | Warehouse |  |  | 1116
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 830
| [Capacity] | [7 empty] | Y | Btu/hr | Nominal Heating Input Capacity Boiler size (Btu/hr) for efficient unit not existing unit
| [EfficiencyRating(base)] | Boiler Input Capacity | < 300,000 Btu/h |  |  |  |  | 84% | N | AFUE | Baseline equiment efficiency rating, depending on boiler input capacity
|  |  | ≥ 300,000 Btu/h and ≤ 2,500,000 Btu/h |  |  |  |  | 80% | N | ET
|  |  | > 2,500,000 Btu/h |  |  |  |  | 82% | N | EC
| [EfficiencyRating(EE)] | [7 empty] | Y |  | Efficiency equiment efficiency rating in Annuel Fuel Utilization Efficiency Rating (AFUE)
| [100,000] | [6 empty] | 100000 | N | Btu/Therm | Converts Btus to Therms
| [ΔTherms] | [7 empty] | C | therm | Therm impact calculated above
| [GCF] | Building Type | Convenience |  |  |  |  | 0.01631 | N | GCF | Gas Coincidence Factor for Heating
|  |  | Education |  |  |  |  | 0.01148
|  |  | Grocery |  |  |  |  | 0.013083
|  |  | Health |  |  |  |  | 0.010179
|  |  | Hospital |  |  |  |  | 0.015543
|  |  | Industrial |  |  |  |  | 0.01424
|  |  | Lodging |  |  |  |  | 0.013205
|  |  | Multifamily |  |  |  |  | 0.012268
|  |  | Office - Large |  |  |  |  | 0.013082
|  |  | Office - Small |  |  |  |  | 0.016718
|  |  | Religious |  |  |  |  | 0.011745
|  |  | Restaurant |  |  |  |  | 0.015262
|  |  | Retail - Large |  |  |  |  | 0.013281
|  |  | Retail - Small |  |  |  |  | 0.014055
|  |  | Warehouse |  |  |  |  | 0.015677
|  |  | Nonresidential Average |  |  |  |  | 0.014623

## Furnace
Furnace
| Measure Code: | NR-HVC-FRNC-V04-200101
| Lifetime of Efficient Equipment: | [6 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
18
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known |  |  | Actual - Baseline
|  | Unknown | AFUE | 85% | N/A
|  |  |  | 86% | 56
|  |  |  | 87% | 113
|  |  |  | 88% | 169
|  |  |  | 89% | 226
|  |  |  | 90% | 282
|  |  |  | 91% | 339
|  |  |  | 92% | 395
|  |  |  | 93% | 452
|  |  |  | 94% | 508
|  |  |  | 95% | 565
|  |  |  | 96% | 858
|  |  |  | 97% | 1151
|  |  |  | 98% | 1444
|  |  |  | 99% | 1738
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | =([EFLH] * [Capacity]* ([AFUE_eff] / [AFUE_base] -[1])) / [100,000]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [EFLH] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1298 | N | Hours | Equivalent Full Load Hours for heating space
[5 empty] | Grocery |  |  | 1493
[5 empty] | Health |  |  | 1206
[5 empty] | Hospital |  |  | 1084
[5 empty] | Lodging |  |  | 1365
[5 empty] | Multifamily |  |  | 1521
[5 empty] | Office - Large |  |  | 1457
[5 empty] | Office - Small |  |  | 1250
[5 empty] | Restaurant |  |  | 1040
[5 empty] | Retail - Large |  |  | 1255
[5 empty] | Retail - Small |  |  | 1172
[5 empty] | Warehouse |  |  | 1277
[5 empty] | Convenience |  |  | 785
[5 empty] | Industrial |  |  | 849
[5 empty] | Religious |  |  | 1322
[5 empty] | Nonresidential Average |  |  | 1251
[5 empty] | Education |  | Zone 6 (Mason City) | 1529
[5 empty] | Grocery |  |  | 1754
[5 empty] | Health |  |  | 1430
[5 empty] | Hospital |  |  | 940
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1846
[5 empty] | Office - Large |  |  | 1748
[5 empty] | Office - Small |  |  | 1435
[5 empty] | Restaurant |  |  | 1324
[5 empty] | Retail - Large |  |  | 1523
[5 empty] | Retail - Small |  |  | 1471
[5 empty] | Warehouse |  |  | 1589
[5 empty] | Convenience |  |  | 1224
[5 empty] | Industrial |  |  | 1275
[5 empty] | Religious |  |  | 1873
[5 empty] | Nonresidential Average |  |  | 1555
[5 empty] | Education |  | Average/Unknown | 1351
[5 empty] | Grocery |  |  | 1601
[5 empty] | Health |  |  | 1346
[5 empty] | Hospital |  |  | 1082
[5 empty] | Lodging |  |  | 1494
[5 empty] | Multifamily |  |  | 1694
[5 empty] | Office - Large |  |  | 1549
[5 empty] | Office - Small |  |  | 1358
[5 empty] | Restaurant |  |  | 1173
[5 empty] | Retail - Large |  |  | 1348
[5 empty] | Retail - Small |  |  | 1372
[5 empty] | Warehouse |  |  | 1443
[5 empty] | Convenience |  |  | 1071
[5 empty] | Industrial |  |  | 1183
[5 empty] | Religious |  |  | 1796
[5 empty] | Nonresidential Average |  |  | 1438
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 510
[5 empty] | Health |  |  | 778
[5 empty] | Hospital |  |  | 1799
[5 empty] | Lodging |  |  | 1080
[5 empty] | Office - Large |  |  | 710
[5 empty] | Office - Small |  |  | 450
[5 empty] | Restaurant |  |  | 896
[5 empty] | Retail - Large |  |  | 709
[5 empty] | Retail - Small |  |  | 785
[5 empty] | Warehouse |  |  | 886
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 690
[5 empty] | Education |  | Zone 6 (Mason City) | 683
[5 empty] | Health |  |  | 972
[5 empty] | Hospital |  |  | 1520
[5 empty] | Lodging |  |  | 1491
[5 empty] | Office - Large |  |  | 917
[5 empty] | Office - Small |  |  | 590
[5 empty] | Restaurant |  |  | 1192
[5 empty] | Retail - Large |  |  | 906
[5 empty] | Retail - Small |  |  | 1036
[5 empty] | Warehouse |  |  | 1238
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 930
[5 empty] | Education |  | Average/Unknown | 591
[5 empty] | Health |  |  | 864
[5 empty] | Hospital |  |  | 2196
[5 empty] | Lodging |  |  | 1471
[5 empty] | Office - Large |  |  | 862
[5 empty] | Office - Small |  |  | 492
[5 empty] | Restaurant |  |  | 1048
[5 empty] | Retail - Large |  |  | 839
[5 empty] | Retail - Small |  |  | 986
[5 empty] | Warehouse |  |  | 1116
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 830
| [Capacity] | [7 empty] | Y | Btu/hr | Nominal Heating Input Capacity Boiler size (Btu/hr) for efficient unit not existing unit
| [AFUEeff] | [7 empty] | Y |  | Annual Fuel Utilization Efficiency Rating (AFUE) for Energy Efficient Equipment
| [AFUEbase] | [6 empty] | 85% | N |  | Annual Fuel Utilization Efficiency Rating (AFUE) for Baseline Equipment
| [100,000] | [6 empty] | 100000 | N | Btu/Therm | Converts Btus to Therms
| [ΔTherms] | [7 empty] | C | therm | Therm impact calculated above
| [GCF] | Building Type | Convenience |  |  |  |  | 0.016482 | N | GCF | Gas Coincidence Factor for Heating
|  |  | Education |  |  |  |  | 0.01148
|  |  | Grocery |  |  |  |  | 0.013083
|  |  | Health |  |  |  |  | 0.010179
|  |  | Hospital |  |  |  |  | 0.015543
|  |  | Industrial |  |  |  |  | 0.014296
|  |  | Lodging |  |  |  |  | 0.013205
|  |  | Multifamily |  |  |  |  | 0.012268
|  |  | Office - Large |  |  |  |  | 0.013082
|  |  | Office - Small |  |  |  |  | 0.016718
|  |  | Religious |  |  |  |  | 0.011964
|  |  | Restaurant |  |  |  |  | 0.015262
|  |  | Retail - Large |  |  |  |  | 0.013281
|  |  | Retail - Small |  |  |  |  | 0.014055
|  |  | Warehouse |  |  |  |  | 0.015677
|  |  | Nonresidential Average |  |  |  |  | 0.014658

## Furnace Blower Motor
Furnace Blower Motor
| Measure Code: | NR-HVC-FBLM-V03-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
20 - furnace age
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Implementation Method | Coupled with Furnace measure | 0
|  | Stand-alone measure, TOS, NC | = $0.29 * [Watts] + 36.50 | Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = ([HP] * [0.746] * [LF_base] * [Hours] * [SF]) / [η_basemotor]
Time of Sale Demand (ΔkW)
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [HP] | [5 empty] | Y | HP | Nominal horsepower of efficient motor
| [0.746] |  |  |  |  | 0.746 | N | HP to Watts | Converts HP to kW
| [Lfbase] |  |  |  |  | 65% | N |  | Load Factor of baseline motor at fan design CFM
| [Hours] |  |  |  |  | 4000 | N | Hours | Annual motor operating hours
| [SF] |  |  |  |  | 0.2 | N |  | Savings factor
| [ηbasemotor] |  |  |  |  | 0.85 | N |  | Efficiency rating of the baseline motor

## Heat Pump Systems
Heat Pump Systems
| Measure Code: | NR-HVC-HPSY-V03-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| CEE Tier 1 |  | $467.99 / ton
| CEE Tier 2 |  | $935.98 / ton
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [Annual kWh Savings_cool] + [Annual kWh Savings_heat]
| Time of Sale Demand (ΔkW) | =[([Capacity_Cool] * (1 / [EER_base] - 1 / [EER_ee])) / [1000]] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options
| ΔkWh | Cooling Capacity | Less than 65 kBtu/hr | = [(EFLH_coo] * [Capacity_Cool] * (1 / [SEER_base] - 1 / [SEER_ee ])) / [1000]] + [([EFLH_Heat] * [Capacity_Heat] * (1 / [HSPF_base] - 1 / [HSFP_ee] )) / [1000]]
|  |  | Greater than 65 kBtu/hr | = [([EFLH_cool] * [Capacity_Cool] * (1 / [E_base] - 1 / [E_ee] )) / [1000]] + [([EFLH_Heat] * [Capacity_Heat] * (1 / [COP_base] - 1 / ([COP_ee ]))) / [3412]]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [EFLHCool] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1073 | N | Hours | Equivalent Full Load Hours for cooling
[5 empty] | Grocery |  |  | 320
[5 empty] | Health |  |  | 1449
[5 empty] | Hospital |  |  | 1792
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1472
[5 empty] | Office - Large |  |  | 1141
[5 empty] | Office - Small |  |  | 986
[5 empty] | Restaurant |  |  | 1397
[5 empty] | Retail - Large |  |  | 846
[5 empty] | Retail - Small |  |  | 891
[5 empty] | Warehouse |  |  | 1032
[5 empty] | Convenience |  |  | 1477
[5 empty] | Industrial |  |  | 1185
[5 empty] | Religious |  |  | 1109
[5 empty] | Nonresidential Average |  |  | 1034
[5 empty] | Education |  | Zone 6 (Mason City) | 848
[5 empty] | Grocery |  |  | 221
[5 empty] | Health |  |  | 996
[5 empty] | Hospital |  |  | 1436
[5 empty] | Lodging |  |  | 1252
[5 empty] | Multifamily |  |  | 1045
[5 empty] | Office - Large |  |  | 843
[5 empty] | Office - Small |  |  | 667
[5 empty] | Restaurant |  |  | 937
[5 empty] | Retail - Large |  |  | 616
[5 empty] | Retail - Small |  |  | 531
[5 empty] | Warehouse |  |  | 539
[5 empty] | Convenience |  |  | 1128
[5 empty] | Industrial |  |  | 856
[5 empty] | Religious |  |  | 797
[5 empty] | Nonresidential Average |  |  | 669
[5 empty] | Education |  | Average/Unknown | 928
[5 empty] | Grocery |  |  | 356
[5 empty] | Health |  |  | 1207
[5 empty] | Hospital |  |  | 1662
[5 empty] | Lodging |  |  | 1460
[5 empty] | Multifamily |  |  | 1349
[5 empty] | Office - Large |  |  | 1084
[5 empty] | Office - Small |  |  | 882
[5 empty] | Restaurant |  |  | 1249
[5 empty] | Retail - Large |  |  | 845
[5 empty] | Retail - Small |  |  | 780
[5 empty] | Warehouse |  |  | 864
[5 empty] | Convenience |  |  | 1351
[5 empty] | Industrial |  |  | 1063
[5 empty] | Religious |  |  | 1031
[5 empty] | Nonresidential Average |  |  | 915
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 776
[5 empty] | Health |  |  | 1482
[5 empty] | Hospital |  |  | 1422
[5 empty] | Lodging |  |  | 1204
[5 empty] | Office - Large |  |  | 816
[5 empty] | Office - Small |  |  | 616
[5 empty] | Restaurant |  |  | 915
[5 empty] | Retail - Large |  |  | 764
[5 empty] | Retail - Small |  |  | 749
[5 empty] | Warehouse |  |  | 223
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 560
[5 empty] | Education |  | Zone 6 (Mason City) | 464
[5 empty] | Health |  |  | 1073
[5 empty] | Hospital |  |  | 946
[5 empty] | Lodging |  |  | 813
[5 empty] | Office - Large |  |  | 641
[5 empty] | Office - Small |  |  | 448
[5 empty] | Restaurant |  |  | 572
[5 empty] | Retail - Large |  |  | 504
[5 empty] | Retail - Small |  |  | 486
[5 empty] | Warehouse |  |  | 35
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 338
[5 empty] | Education |  | Average/Unknown | 645
[5 empty] | Health |  |  | 1328
[5 empty] | Hospital |  |  | 1356
[5 empty] | Lodging |  |  | 1105
[5 empty] | Office - Large |  |  | 823
[5 empty] | Office - Small |  |  | 542
[5 empty] | Restaurant |  |  | 825
[5 empty] | Retail - Large |  |  | 711
[5 empty] | Retail - Small |  |  | 744
[5 empty] | Warehouse |  |  | 148
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 488
| [CapacityCool] | [7 empty] | Y | Btu/hr | Cooling Capacity for Air Source Heat Pump, 1 ton = 12000 Btu/hr
| [SEERbase] | [7 empty] | N |  | Seasonal Energy Efficiency Ratio of the baseline equipment. See table in TRM.
| [SEERee] | [7 empty] | Y |  | Seasonal Energy Efficiency Ratio of the energy efficient equipment
| [EFLHHeat] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1298 | N | Hours | Equivalent Full Load Hours for heating space
[5 empty] | Grocery |  |  | 1493
[5 empty] | Health |  |  | 1206
[5 empty] | Hospital |  |  | 1084
[5 empty] | Lodging |  |  | 1365
[5 empty] | Multifamily |  |  | 1521
[5 empty] | Office - Large |  |  | 1457
[5 empty] | Office - Small |  |  | 1250
[5 empty] | Restaurant |  |  | 1040
[5 empty] | Retail - Large |  |  | 1255
[5 empty] | Retail - Small |  |  | 1172
[5 empty] | Warehouse |  |  | 1277
[5 empty] | Convenience |  |  | 785
[5 empty] | Industrial |  |  | 849
[5 empty] | Religious |  |  | 1322
[5 empty] | Nonresidential Average |  |  | 1251
[5 empty] | Education |  | Zone 6 (Mason City) | 1529
[5 empty] | Grocery |  |  | 1754
[5 empty] | Health |  |  | 1430
[5 empty] | Hospital |  |  | 940
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1846
[5 empty] | Office - Large |  |  | 1748
[5 empty] | Office - Small |  |  | 1435
[5 empty] | Restaurant |  |  | 1324
[5 empty] | Retail - Large |  |  | 1523
[5 empty] | Retail - Small |  |  | 1471
[5 empty] | Warehouse |  |  | 1589
[5 empty] | Convenience |  |  | 1224
[5 empty] | Industrial |  |  | 1275
[5 empty] | Religious |  |  | 1873
[5 empty] | Nonresidential Average |  |  | 1555
[5 empty] | Education |  | Average/Unknown | 1351
[5 empty] | Grocery |  |  | 1601
[5 empty] | Health |  |  | 1346
[5 empty] | Hospital |  |  | 1082
[5 empty] | Lodging |  |  | 1494
[5 empty] | Multifamily |  |  | 1694
[5 empty] | Office - Large |  |  | 1549
[5 empty] | Office - Small |  |  | 1358
[5 empty] | Restaurant |  |  | 1173
[5 empty] | Retail - Large |  |  | 1348
[5 empty] | Retail - Small |  |  | 1372
[5 empty] | Warehouse |  |  | 1443
[5 empty] | Convenience |  |  | 1071
[5 empty] | Industrial |  |  | 1183
[5 empty] | Religious |  |  | 1796
[5 empty] | Nonresidential Average |  |  | 1438
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 510
[5 empty] | Health |  |  | 778
[5 empty] | Hospital |  |  | 1799
[5 empty] | Lodging |  |  | 1080
[5 empty] | Office - Large |  |  | 710
[5 empty] | Office - Small |  |  | 450
[5 empty] | Restaurant |  |  | 896
[5 empty] | Retail - Large |  |  | 709
[5 empty] | Retail - Small |  |  | 785
[5 empty] | Warehouse |  |  | 886
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 690
[5 empty] | Education |  | Zone 6 (Mason City) | 683
[5 empty] | Health |  |  | 972
[5 empty] | Hospital |  |  | 1520
[5 empty] | Lodging |  |  | 1491
[5 empty] | Office - Large |  |  | 917
[5 empty] | Office - Small |  |  | 590
[5 empty] | Restaurant |  |  | 1192
[5 empty] | Retail - Large |  |  | 906
[5 empty] | Retail - Small |  |  | 1036
[5 empty] | Warehouse |  |  | 1238
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 930
[5 empty] | Education |  | Average/Unknown | 591
[5 empty] | Health |  |  | 864
[5 empty] | Hospital |  |  | 2196
[5 empty] | Lodging |  |  | 1471
[5 empty] | Office - Large |  |  | 862
[5 empty] | Office - Small |  |  | 492
[5 empty] | Restaurant |  |  | 1048
[5 empty] | Retail - Large |  |  | 839
[5 empty] | Retail - Small |  |  | 986
[5 empty] | Warehouse |  |  | 1116
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 830
| [CapacityHeat] | [7 empty] | Y | Btu/hr | Full Load Heating Capacity of Air Source Heat Pump (1 ton = 12,000 Btu/hr)
| [HSPFbase] | [7 empty] | N |  | Heating Seasonal Performance Factor of the baseline equipment. See table in TRM
| [HSPFee] | [7 empty] | Y |  | Heating Seasonal Performance Factor of the energy efficient equipment
| [Ebase] | [7 empty] | N |  | Baseline equipment efficiency. Use Integrated Energy Efficiency Ratio (IEER), except in instances of water source units, where Energy Efficiency Ratio (EER) shall be used. See table in TRM
| [Eee] | [7 empty] | Y |  | Efficient equipment efficiency. Use Integrated Energy Efficiency Ratio (IEER), except in instances of water source units, where Energy Efficiency Ratio (EER) shall be used.
| [3412] | [6 empty] | 3412 | N | kBtu per kWh | kBtu per kWh
| [COPbase] | [7 empty] | N |  | Coefficient of performance of the baseline equipment, see table in TRM
| [COPee] | [7 empty] | Y |  | Coefficient of performance of the energy efficient equipment
| [EERbase] | [9 empty] | Energy Efficiency Ratio of the baseline equipment; see table in TRM. Since EER requirements for air-cooled heat pumps < 65 kBtu/hr are not specified, assume the following conversion from SEER to EER: EER = -0.02 * SEER2 + 1.12 * SEER.
| [EERee] | [9 empty] | Energy Efficiency Ratio of the energy efficient equipment. For air-cooled air conditioners < 65 kBtu/hr, if the actual EERee is unknown, assume the following conversion from SEER to EER: EER = –0.02 × SEER² + 1.12 × SEER.
| [CF] | Building Type | Convenience |  |  |  |  | 92.3% | N |  | Summer Peak Coincidence Factor for Cooling
|  |  | Education |  |  |  |  | 96.7%
|  |  | Grocery |  |  |  |  | 100%
|  |  | Health |  |  |  |  | 100%
|  |  | Hospital |  |  |  |  | 98.6%
|  |  | Industrial |  |  |  |  | 44.6%
|  |  | Lodging |  |  |  |  | 97.4%
|  |  | Multifamily |  |  |  |  | 100%
|  |  | Office - Large |  |  |  |  | 98.8%
|  |  | Office - Small |  |  |  |  | 100%
|  |  | Religious |  |  |  |  | 94.3%
|  |  | Restaurant |  |  |  |  | 99.6%
|  |  | Retail - Large |  |  |  |  | 87.6%
|  |  | Retail - Small |  |  |  |  | 100%
|  |  | Warehouse |  |  |  |  | 77.9%
|  |  | Nonresidential Average |  |  |  |  | 92.3%

## Geothermal Source Heat Pump
Geothermal Source Heat Pump
| Measure Code: | NR-HVAC-GSHP-V03-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
25
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Cost Known | Actual minus $1867 per ton of capacity
|  | Cost Unknown | $4081 per ton minus $1867 per ton of capacity
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [([EFLH_Cool] * [Capacity_Cool] * ([PLF_Cool] * (1 / [EER_Base] – 1 / [EEREE-PL] )+ [FLF_Cool] * (1 / [EER_Base] – 1 / [EEREE-FL] ))) / [1000]] + [([EFLH_Heat] * [Capacity_Heat] * ([PLF_Heat] * (1 / [HSPF_Base] – 1 / (([COPEE- PL] * [3.412]) )) + [FLF_Heat] * (1 / [HSPF_Base] – 1 / (([COPEE- FL] * [3.412]) )))) / [1000]]
| Time of Sale Demand (ΔkW) | = (([Capacity_Cool] * (1 / [EER_base] - 1 / [EEREE-FL] )) / [1000]) * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [EEREE - PL] | System type | Closed loop | = 0.0000315 * [EER]^3 - 0.0111 * [EER]^2 + 0.959*[EER]
|  |  | Open loop | = 0.00005 * [EER]^3 - 0.0145 * [EER]^2 + 0.93 * [EER]
| [EEREE - FL] | System type | Closed loop | = 0.0000315 * [EER]^3 - 0.0111 * [EER]^2 + 0.959*[EER]
|  |  | Open loop | = 0.00005 * [EER]^3 - 0.0145 * [EER]^2 + 0.93 * [EER]
| [COPEE - PL] | System type | Closed loop | = 0.000416 * [COP]^3 - 0.041 * [COP]^2 + 1.0086 * [COP]
|  |  | Open loop | = 0.00067 * [COP]^3 - 0.0531 * [COP]^2 + 0.976 * [COP]
| [COPEE - FL] | System type | Closed loop | = 0.000416 * [COP]^3 - 0.041 * [COP]^2 + 1.0086 * [COP]
|  |  | Open loop | = 0.00067 * [COP]^3 - 0.0531 * [COP]^2 + 0.976 * [COP]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [EFLHCool] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1073 | N | Hours | Equivalent Full Load Hours for cooling
[5 empty] | Grocery |  |  | 320
[5 empty] | Health |  |  | 1449
[5 empty] | Hospital |  |  | 1792
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1472
[5 empty] | Office - Large |  |  | 1141
[5 empty] | Office - Small |  |  | 986
[5 empty] | Restaurant |  |  | 1397
[5 empty] | Retail - Large |  |  | 846
[5 empty] | Retail - Small |  |  | 891
[5 empty] | Warehouse |  |  | 1032
[5 empty] | Convenience |  |  | 1477
[5 empty] | Industrial |  |  | 1185
[5 empty] | Religious |  |  | 1109
[5 empty] | Nonresidential Average |  |  | 1034
[5 empty] | Education |  | Zone 6 (Mason City) | 848
[5 empty] | Grocery |  |  | 221
[5 empty] | Health |  |  | 996
[5 empty] | Hospital |  |  | 1436
[5 empty] | Lodging |  |  | 1252
[5 empty] | Multifamily |  |  | 1045
[5 empty] | Office - Large |  |  | 843
[5 empty] | Office - Small |  |  | 667
[5 empty] | Restaurant |  |  | 937
[5 empty] | Retail - Large |  |  | 616
[5 empty] | Retail - Small |  |  | 531
[5 empty] | Warehouse |  |  | 539
[5 empty] | Convenience |  |  | 1128
[5 empty] | Industrial |  |  | 856
[5 empty] | Religious |  |  | 797
[5 empty] | Nonresidential Average |  |  | 669
[5 empty] | Education |  | Average/Unknown | 928
[5 empty] | Grocery |  |  | 356
[5 empty] | Health |  |  | 1207
[5 empty] | Hospital |  |  | 1662
[5 empty] | Lodging |  |  | 1460
[5 empty] | Multifamily |  |  | 1349
[5 empty] | Office - Large |  |  | 1084
[5 empty] | Office - Small |  |  | 882
[5 empty] | Restaurant |  |  | 1249
[5 empty] | Retail - Large |  |  | 845
[5 empty] | Retail - Small |  |  | 780
[5 empty] | Warehouse |  |  | 864
[5 empty] | Convenience |  |  | 1351
[5 empty] | Industrial |  |  | 1063
[5 empty] | Religious |  |  | 1031
[5 empty] | Nonresidential Average |  |  | 915
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 776
[5 empty] | Health |  |  | 1482
[5 empty] | Hospital |  |  | 1422
[5 empty] | Lodging |  |  | 1204
[5 empty] | Office - Large |  |  | 816
[5 empty] | Office - Small |  |  | 616
[5 empty] | Restaurant |  |  | 915
[5 empty] | Retail - Large |  |  | 764
[5 empty] | Retail - Small |  |  | 749
[5 empty] | Warehouse |  |  | 223
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 560
[5 empty] | Education |  | Zone 6 (Mason City) | 464
[5 empty] | Health |  |  | 1073
[5 empty] | Hospital |  |  | 946
[5 empty] | Lodging |  |  | 813
[5 empty] | Office - Large |  |  | 641
[5 empty] | Office - Small |  |  | 448
[5 empty] | Restaurant |  |  | 572
[5 empty] | Retail - Large |  |  | 504
[5 empty] | Retail - Small |  |  | 486
[5 empty] | Warehouse |  |  | 35
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 338
[5 empty] | Education |  | Average/Unknown | 645
[5 empty] | Health |  |  | 1328
[5 empty] | Hospital |  |  | 1356
[5 empty] | Lodging |  |  | 1105
[5 empty] | Office - Large |  |  | 823
[5 empty] | Office - Small |  |  | 542
[5 empty] | Restaurant |  |  | 825
[5 empty] | Retail - Large |  |  | 711
[5 empty] | Retail - Small |  |  | 744
[5 empty] | Warehouse |  |  | 148
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 488
| [CapacityCool] | [7 empty] | Y | Btu/hr | Cooling Capacity for Geothermal Source Heat Pump, 1 ton = 12000 Btu/hr
| [PLFCool] | Speed | Variable |  |  |  |  | 0.85 | N |  | Part load cooling mode operation
|  |  | Single/Constant |  |  |  |  | 0
| [FLFCool ] | Speed | Variable |  |  |  |  | 0.15 | N |  | Full load cooling mode operation factor
|  |  | Single/Constant |  |  |  |  | 1
| [EERBase] | Equipment Type | Small Commercial Package Air-Conditioning and Heating Equipment (Air-Cooled, 3-Phase, Split System) | Heating Type | All |  |  | 11.8 | Y |  | EER Efficiency of new baseline AHSP unit
|  |  | Small Commercial Package Air-Conditioning and Heating Equipment (Air-Cooled, 3-Phase, Single-Package) |  | All |  |  | 11.8
|  |  | Small Commercial Packaged Air Conditioning and Heating Equipment (Air Cooled) |  | Electric Resistance Heating or No Heating |  |  | 12
[5 empty] | All Other Types of Heating |  |  | 11.8
|  |  | Large Commercial Packaged Air Conditioning and Heating Equipment (Air Cooled) |  | Electric Resistance Heating or No Heating |  |  | 11.4
[5 empty] | All Other Types of Heating |  |  | 11.2
|  |  | Very Large Commercial Packaged Air Conditioning and Heating Equipment (Air Cooled) |  | Electric Resistance Heating or No Heating |  |  | 10.5
[5 empty] | All Other Types of Heating |  |  | 10.3
| [EEREE - PL] | [7 empty] | C |  | Full Load EER Efficiency of ENERGY STAR GSHP unit
| [EFLHHeat] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1298 | N | Hours | Equivalent Full Load Hours for heating space
[5 empty] | Grocery |  |  | 1493
[5 empty] | Health |  |  | 1206
[5 empty] | Hospital |  |  | 1084
[5 empty] | Lodging |  |  | 1365
[5 empty] | Multifamily |  |  | 1521
[5 empty] | Office - Large |  |  | 1457
[5 empty] | Office - Small |  |  | 1250
[5 empty] | Restaurant |  |  | 1040
[5 empty] | Retail - Large |  |  | 1255
[5 empty] | Retail - Small |  |  | 1172
[5 empty] | Warehouse |  |  | 1277
[5 empty] | Convenience |  |  | 785
[5 empty] | Industrial |  |  | 849
[5 empty] | Religious |  |  | 1322
[5 empty] | Nonresidential Average |  |  | 1251
[5 empty] | Education |  | Zone 6 (Mason City) | 1529
[5 empty] | Grocery |  |  | 1754
[5 empty] | Health |  |  | 1430
[5 empty] | Hospital |  |  | 940
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1846
[5 empty] | Office - Large |  |  | 1748
[5 empty] | Office - Small |  |  | 1435
[5 empty] | Restaurant |  |  | 1324
[5 empty] | Retail - Large |  |  | 1523
[5 empty] | Retail - Small |  |  | 1471
[5 empty] | Warehouse |  |  | 1589
[5 empty] | Convenience |  |  | 1224
[5 empty] | Industrial |  |  | 1275
[5 empty] | Religious |  |  | 1873
[5 empty] | Nonresidential Average |  |  | 1555
[5 empty] | Education |  | Average/Unknown | 1351
[5 empty] | Grocery |  |  | 1601
[5 empty] | Health |  |  | 1346
[5 empty] | Hospital |  |  | 1082
[5 empty] | Lodging |  |  | 1494
[5 empty] | Multifamily |  |  | 1694
[5 empty] | Office - Large |  |  | 1549
[5 empty] | Office - Small |  |  | 1358
[5 empty] | Restaurant |  |  | 1173
[5 empty] | Retail - Large |  |  | 1348
[5 empty] | Retail - Small |  |  | 1372
[5 empty] | Warehouse |  |  | 1443
[5 empty] | Convenience |  |  | 1071
[5 empty] | Industrial |  |  | 1183
[5 empty] | Religious |  |  | 1796
[5 empty] | Nonresidential Average |  |  | 1438
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 510
[5 empty] | Health |  |  | 778
[5 empty] | Hospital |  |  | 1799
[5 empty] | Lodging |  |  | 1080
[5 empty] | Office - Large |  |  | 710
[5 empty] | Office - Small |  |  | 450
[5 empty] | Restaurant |  |  | 896
[5 empty] | Retail - Large |  |  | 709
[5 empty] | Retail - Small |  |  | 785
[5 empty] | Warehouse |  |  | 886
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 690
[5 empty] | Education |  | Zone 6 (Mason City) | 683
[5 empty] | Health |  |  | 972
[5 empty] | Hospital |  |  | 1520
[5 empty] | Lodging |  |  | 1491
[5 empty] | Office - Large |  |  | 917
[5 empty] | Office - Small |  |  | 590
[5 empty] | Restaurant |  |  | 1192
[5 empty] | Retail - Large |  |  | 906
[5 empty] | Retail - Small |  |  | 1036
[5 empty] | Warehouse |  |  | 1238
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 930
[5 empty] | Education |  | Average/Unknown | 591
[5 empty] | Health |  |  | 864
[5 empty] | Hospital |  |  | 2196
[5 empty] | Lodging |  |  | 1471
[5 empty] | Office - Large |  |  | 862
[5 empty] | Office - Small |  |  | 492
[5 empty] | Restaurant |  |  | 1048
[5 empty] | Retail - Large |  |  | 839
[5 empty] | Retail - Small |  |  | 986
[5 empty] | Warehouse |  |  | 1116
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 830
| [CapacityHeat] | [7 empty] | Y | Btu/hr | Full Load Heating Capacity of Geothermal Source Heat Pump (1 ton = 12,000 Btu/hr)
| [PLFHeat] | Speed | Variable |  |  |  |  | 0.5 | N |  | Part load heating mode operation
|  |  | Single/Constant |  |  |  |  | 0
| [FLFHeat] | Speed | Variable |  |  |  |  | 0.5 | N |  | Full load heating mode operation
|  |  | Single/Constant |  |  |  |  | 1
| [HSPFBase] | Equipment Type | Small Commercial Package Air-Conditioning and Heating Equipment (Air-Cooled, 3-Phase, Split System) | Heating Type | All |  |  | 8.2 | Y |  | Heating System Performance Factor of new replacement baseline heating system
|  |  | Small Commercial Package Air-Conditioning and Heating Equipment (Air-Cooled, 3-Phase, Single-Package) |  | All |  |  | 8
|  |  | Small Commercial Packaged Air Conditioning and Heating Equipment (Air Cooled) |  | Electric Resistance Heating or No Heating
[5 empty] | All Other Types of Heating |  |  | 11.2596
|  |  | Large Commercial Packaged Air Conditioning and Heating Equipment (Air Cooled) |  | Electric Resistance Heating or No Heating
[5 empty] | All Other Types of Heating |  |  | 10.9184
|  |  | Very Large Commercial Packaged Air Conditioning and Heating Equipment (Air Cooled) |  | Electric Resistance Heating or No Heating
[5 empty] | All Other Types of Heating |  |  | 10.9184
| [COPEE - PL ] | [7 empty] | C |  | Part Load Coeffcient of Performance of efficient unit
| [3.412] | [6 empty] | 3.412 | N |  | Constant to ocnvert the COP of the unit to the Heating Season Performance Factor (HSPF)
| [EEREE - FL] | [7 empty] | C |  | Full Load EER Efficiency of ENERGY STAR GSHP unit
| [COPEE - FL ] | [7 empty] | C |  | Full Load Coeffcient of Performance of efficient unit
| [CF] | Building Type | Convenience |  |  |  |  | 92.3% | N |  | Summer System Peak Coincidence Factor for Cooling
|  |  | Education |  |  |  |  | 96.7%
|  |  | Grocery |  |  |  |  | 100%
|  |  | Health |  |  |  |  | 100%
|  |  | Hospital |  |  |  |  | 98.6%
|  |  | Industrial |  |  |  |  | 44.6%
|  |  | Lodging |  |  |  |  | 97.4%
|  |  | Multifamily |  |  |  |  | 100%
|  |  | Office - Large |  |  |  |  | 98.8%
|  |  | Office - Small |  |  |  |  | 100%
|  |  | Religious |  |  |  |  | 94.3%
|  |  | Restaurant |  |  |  |  | 99.6%
|  |  | Retail - Large |  |  |  |  | 87.6%
|  |  | Retail - Small |  |  |  |  | 100%
|  |  | Warehouse |  |  |  |  | 77.9%
|  |  | Nonresidential Average |  |  |  |  | 92.3%

## Sing-Pack and Split Sys Uni AC
Sing-Pack and Split Sys Uni AC
| Measure Code: | NR-HVC-SPUA-V04-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Efficiency Level | CEE Tier 1 | Capacity | < 135,000 Btu/hr | $63.42 / ton
|  |  |  | 135,000 Btu/hr to > 250,000 Btu/hr | $63.42 / ton
|  |  |  | 250,000 Btu/hr and greater | $18.92 / ton
|  | CEE Tier 2 |  | < 135,000 Btu/hr | $126.84 / ton
|  |  |  | 135,000 Btu/hr to > 250,000 Btu/hr | $126.84 / ton
|  |  |  | 250,000 Btu/hr and greater | $37.83 / ton
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = (([EFLH_cool] * [Capacity_Cool] * (1/[EFF_base] - 1/[EFF_ee] ))/1000)
| Time of Sale Demand (ΔkW) | = (([Capacity_Cool] * (1/[EER_base] - 1/[EER_ee]))/1000) * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [CapacityCool] | [7 empty] | Y |  | Cooling Capacity of new equipment in Btu/hr (note 1 ton = 12,000Btu/hr)
| [EFFbase] | Cooling Capacity | <65 kBtu/h | [5 empty] | N | SEER | Seasonal Energy Efficiency Ratio of baseline unit (kBtu/kWh); see table in TRM for default values
|  |  | >65 kBtu/h | [6 empty] | IEER | Integrated Energy Efficiency Ratio of baseline unit (kBtu/kWh); see table below in TTM got default values
| [EFFee] | Cooling Capacity | <65 kBtu/h | [5 empty] | Y | SEER | Seasonal Energy Efficiency Ratio of ENERGY STAR unit (kBtu/kWh)
|  |  | >65 kBtu/h | [6 empty] | IEER | Integrated Energy Efficiency Ratio of ENERGY STAR unit (kBtu/kWh)
| [EFLHCool] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1073 | N | Hours | Equivalent Full Load Hours for cooling
[5 empty] | Grocery |  |  | 320
[5 empty] | Health |  |  | 1449
[5 empty] | Hospital |  |  | 1792
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1472
[5 empty] | Office - Large |  |  | 1141
[5 empty] | Office - Small |  |  | 986
[5 empty] | Restaurant |  |  | 1397
[5 empty] | Retail - Large |  |  | 846
[5 empty] | Retail - Small |  |  | 891
[5 empty] | Warehouse |  |  | 1032
[5 empty] | Convenience |  |  | 1477
[5 empty] | Industrial |  |  | 1185
[5 empty] | Religious |  |  | 1109
[5 empty] | Nonresidential Average |  |  | 1034
[5 empty] | Education |  | Zone 6 (Mason City) | 848
[5 empty] | Grocery |  |  | 221
[5 empty] | Health |  |  | 996
[5 empty] | Hospital |  |  | 1436
[5 empty] | Lodging |  |  | 1252
[5 empty] | Multifamily |  |  | 1045
[5 empty] | Office - Large |  |  | 843
[5 empty] | Office - Small |  |  | 667
[5 empty] | Restaurant |  |  | 937
[5 empty] | Retail - Large |  |  | 616
[5 empty] | Retail - Small |  |  | 531
[5 empty] | Warehouse |  |  | 539
[5 empty] | Convenience |  |  | 1128
[5 empty] | Industrial |  |  | 856
[5 empty] | Religious |  |  | 797
[5 empty] | Nonresidential Average |  |  | 669
[5 empty] | Education |  | Average/Unknown | 928
[5 empty] | Grocery |  |  | 356
[5 empty] | Health |  |  | 1207
[5 empty] | Hospital |  |  | 1662
[5 empty] | Lodging |  |  | 1460
[5 empty] | Multifamily |  |  | 1349
[5 empty] | Office - Large |  |  | 1084
[5 empty] | Office - Small |  |  | 882
[5 empty] | Restaurant |  |  | 1249
[5 empty] | Retail - Large |  |  | 845
[5 empty] | Retail - Small |  |  | 780
[5 empty] | Warehouse |  |  | 864
[5 empty] | Convenience |  |  | 1351
[5 empty] | Industrial |  |  | 1063
[5 empty] | Religious |  |  | 1031
[5 empty] | Nonresidential Average |  |  | 915
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 776
[5 empty] | Health |  |  | 1482
[5 empty] | Hospital |  |  | 1422
[5 empty] | Lodging |  |  | 1204
[5 empty] | Office - Large |  |  | 816
[5 empty] | Office - Small |  |  | 616
[5 empty] | Restaurant |  |  | 915
[5 empty] | Retail - Large |  |  | 764
[5 empty] | Retail - Small |  |  | 749
[5 empty] | Warehouse |  |  | 223
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 560
[5 empty] | Education |  | Zone 6 (Mason City) | 464
[5 empty] | Health |  |  | 1073
[5 empty] | Hospital |  |  | 946
[5 empty] | Lodging |  |  | 813
[5 empty] | Office - Large |  |  | 641
[5 empty] | Office - Small |  |  | 448
[5 empty] | Restaurant |  |  | 572
[5 empty] | Retail - Large |  |  | 504
[5 empty] | Retail - Small |  |  | 486
[5 empty] | Warehouse |  |  | 35
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 338
[5 empty] | Education |  | Average/Unknown | 645
[5 empty] | Health |  |  | 1328
[5 empty] | Hospital |  |  | 1356
[5 empty] | Lodging |  |  | 1105
[5 empty] | Office - Large |  |  | 823
[5 empty] | Office - Small |  |  | 542
[5 empty] | Restaurant |  |  | 825
[5 empty] | Retail - Large |  |  | 711
[5 empty] | Retail - Small |  |  | 744
[5 empty] | Warehouse |  |  | 148
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 488
| [EERbase] | [7 empty] | N | EER | Energy Efficiency Ratio of the baseline equipment; see table in TRM. Since IECC 2012 does not provide EER requirements for air-cooled air conditioners < 65 kBtu/hr, assume the following conversion from SEER to EER: EER = –0.02 × SEER² + 1.12 × SEER
| [EERee] | [7 empty] | Y | EER | Energy Efficiency Ratio of the energy efficient equipment. For air-cooled air conditioners < 65 kBtu/hr, if the actual EERee is unknown, assume the following conversion from SEER to EER: EER = –0.02 × SEER² + 1.12 × SEER
| [CF] | Building Type | Convenience |  |  |  |  | 92.3% | N |  | Summer Peak Coincidence Factor for Cooling
|  |  | Education |  |  |  |  | 96.7%
|  |  | Grocery |  |  |  |  | 100%
|  |  | Health |  |  |  |  | 100%
|  |  | Hospital |  |  |  |  | 98.6%
|  |  | Industrial |  |  |  |  | 44.6%
|  |  | Lodging |  |  |  |  | 97.4%
|  |  | Multifamily |  |  |  |  | 100%
|  |  | Office - Large |  |  |  |  | 98.8%
|  |  | Office - Small |  |  |  |  | 100%
|  |  | Religious |  |  |  |  | 94.3%
|  |  | Restaurant |  |  |  |  | 99.6%
|  |  | Retail - Large |  |  |  |  | 87.6%
|  |  | Retail - Small |  |  |  |  | 100%
|  |  | Warehouse |  |  |  |  | 77.9%
|  |  | Nonresidential Average |  |  |  |  | 92.3%

## Electric Chiller
Electric Chiller
| Measure Code: | NR-HVC-CHIL-V02-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
20
Measure Cost:
| Air cooled, electrically operated ($/ton) | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost (per ton) | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Efficiency Range | < 9.9 EER | Capacity (tons) | < 50 | 137
|  |  |  | >= 50 and <100 | 69
|  |  |  | >= 100 and <150 | 46
|  |  |  | >= 150 and <200 | 34
|  |  |  | >= 200 | 17
|  | 9.9 EER and < 10.2 EER |  | < 50 | 259
|  |  |  | >= 50 and <100 | 129
|  |  |  | >= 100 and <150 | 86
|  |  |  | >= 150 and <200 | 65
|  |  |  | >= 200 | 32
|  | 10.2 EER and < 10.52 EER |  | < 50 | 350
|  |  |  | >= 50 and <100 | 175
|  |  |  | >= 100 and <150 | 117
|  |  |  | >= 150 and <200 | 88
|  |  |  | >= 200 | 44
|  | 10.52 EER and greater |  | < 50 | 411
|  |  |  | >= 50 and <100 | 206
|  |  |  | >= 100 and <150 | 137
|  |  |  | >= 150 and <200 | 103
|  |  |  | >= 200 | 51
Water cooled, electrically operated, positive displacement (rotary screw and scroll) ($/ton)
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost (per ton) | Full Cost (Early Replacement)
| Efficiency Range | > 0.72 kW/ton | Capacity (tons) | < 50 | 311
|  |  |  | >= 50 and <100 | 143
|  |  |  | >= 100 and <150 | n/a
|  |  |  | >= 150 and <200 | n/a
|  |  |  | >= 200 | n/a
|  | 0.72 and > 0.68 kW/ton |  | < 50 | 518
|  |  |  | >= 50 and <100 | 246
|  |  |  | >= 100 and <150 | n/a
|  |  |  | >= 150 and <200 | n/a
|  |  |  | >= 200 | n/a
|  | 0.68 and >0.64 kW/ton |  | < 50 | n/a
|  |  |  | >= 50 and <100 | n/a
|  |  |  | >= 100 and <150 | n/a
|  |  |  | >= 150 and <200 | 52
|  |  |  | >= 200 | n/a
|  | 0.64 kW/ton and less |  | < 50 | n/a
|  |  |  | >= 50 and <100 | n/a
|  |  |  | >= 100 and <150 | n/a
|  |  |  | >= 150 and <200 | 104
|  |  |  | >= 200 | 13
Water cooled, electrically operated, positive displacement (reciprocating) ($/ton)
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost (per ton) | Full Cost (Early Replacement)
| Efficiency Range | > 0.60 kW/ton | Capacity (tons) | < 100 | 88
|  |  |  | >= 100 and <150 | 59
|  |  |  | >= 150 and <200 | 44
|  |  |  | >= 200 and <300 | n/a
|  |  |  | >= 300 | n/a
|  | 0.60 and > 0.58 kW/ton |  | < 100 | 140
|  |  |  | >= 100 and <150 | 93
|  |  |  | >= 150 and <200 | 70
|  |  |  | >= 200 and <300 | n/a
|  |  |  | >= 300 | n/a
|  | 0.58 kw/ton and less |  | < 100 | 244
|  |  |  | >= 100 and <150 | 162
|  |  |  | >= 150 and <200 | 122
|  |  |  | >= 200 and <300 | 31
|  |  |  | >= 300 | 13
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [TONS] * (([IPLVbase]) – ([IPLVee])) * [EFLH]
| Time of Sale Demand (ΔkW) | = [TONS] * (([PEbase]) – ([PEee])) * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [TONS] | [7 empty] | Y | Tons | Chiller nominal cooling capacity in tons (note: 1 ton = 12,000 Btu/hr)
| [IPLVbase] | [7 empty] | N | kW/ton | Efficiency of baseline equipment expressed as Integrated Part Load Value(kW/ton). Chiller units are dependent on chiller type. See ‘Chiller Units, Convertion Values’ and ‘Baseline Efficiency Values by Chiller Type’ and Capacity in the Reference Tables section.
| [IPLVee] | [7 empty] | Y | kW/ton | Efficiency of high efficiency equipment expressed as Integrated Part Load Value
| [EFLHCool] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1073 | N | Hours | Equivalent Full Load Hours for cooling
[5 empty] | Grocery |  |  | 320
[5 empty] | Health |  |  | 1449
[5 empty] | Hospital |  |  | 1792
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1472
[5 empty] | Office - Large |  |  | 1141
[5 empty] | Office - Small |  |  | 986
[5 empty] | Restaurant |  |  | 1397
[5 empty] | Retail - Large |  |  | 846
[5 empty] | Retail - Small |  |  | 891
[5 empty] | Warehouse |  |  | 1032
[5 empty] | Convenience |  |  | 1477
[5 empty] | Industrial |  |  | 1185
[5 empty] | Religious |  |  | 1109
[5 empty] | Nonresidential Average |  |  | 1034
[5 empty] | Education |  | Zone 6 (Mason City) | 848
[5 empty] | Grocery |  |  | 221
[5 empty] | Health |  |  | 996
[5 empty] | Hospital |  |  | 1436
[5 empty] | Lodging |  |  | 1252
[5 empty] | Multifamily |  |  | 1045
[5 empty] | Office - Large |  |  | 843
[5 empty] | Office - Small |  |  | 667
[5 empty] | Restaurant |  |  | 937
[5 empty] | Retail - Large |  |  | 616
[5 empty] | Retail - Small |  |  | 531
[5 empty] | Warehouse |  |  | 539
[5 empty] | Convenience |  |  | 1128
[5 empty] | Industrial |  |  | 856
[5 empty] | Religious |  |  | 797
[5 empty] | Nonresidential Average |  |  | 669
[5 empty] | Education |  | Average/Unknown | 928
[5 empty] | Grocery |  |  | 356
[5 empty] | Health |  |  | 1207
[5 empty] | Hospital |  |  | 1662
[5 empty] | Lodging |  |  | 1460
[5 empty] | Multifamily |  |  | 1349
[5 empty] | Office - Large |  |  | 1084
[5 empty] | Office - Small |  |  | 882
[5 empty] | Restaurant |  |  | 1249
[5 empty] | Retail - Large |  |  | 845
[5 empty] | Retail - Small |  |  | 780
[5 empty] | Warehouse |  |  | 864
[5 empty] | Convenience |  |  | 1351
[5 empty] | Industrial |  |  | 1063
[5 empty] | Religious |  |  | 1031
[5 empty] | Nonresidential Average |  |  | 915
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 776
[5 empty] | Health |  |  | 1482
[5 empty] | Hospital |  |  | 1422
[5 empty] | Lodging |  |  | 1204
[5 empty] | Office - Large |  |  | 816
[5 empty] | Office - Small |  |  | 616
[5 empty] | Restaurant |  |  | 915
[5 empty] | Retail - Large |  |  | 764
[5 empty] | Retail - Small |  |  | 749
[5 empty] | Warehouse |  |  | 223
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 560
[5 empty] | Education |  | Zone 6 (Mason City) | 464
[5 empty] | Health |  |  | 1073
[5 empty] | Hospital |  |  | 946
[5 empty] | Lodging |  |  | 813
[5 empty] | Office - Large |  |  | 641
[5 empty] | Office - Small |  |  | 448
[5 empty] | Restaurant |  |  | 572
[5 empty] | Retail - Large |  |  | 504
[5 empty] | Retail - Small |  |  | 486
[5 empty] | Warehouse |  |  | 35
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 338
[5 empty] | Education |  | Average/Unknown | 645
[5 empty] | Health |  |  | 1328
[5 empty] | Hospital |  |  | 1356
[5 empty] | Lodging |  |  | 1105
[5 empty] | Office - Large |  |  | 823
[5 empty] | Office - Small |  |  | 542
[5 empty] | Restaurant |  |  | 825
[5 empty] | Retail - Large |  |  | 711
[5 empty] | Retail - Small |  |  | 744
[5 empty] | Warehouse |  |  | 148
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 488
| [PEbase] | [7 empty] | N | kW/ton | Peak efficiency of baseline equipment expressed as Full Load (kW/ton). Please see reference table in TRM.
| [PEee] | [7 empty] | Y | kW/ton | Peak efficiency of high efficiency equipment expressed as Full Load (kW/ton)
| [CF] | Building Type | Convenience |  |  |  |  | 92.3% | N |  | Summer Peak Coincidence Factor for Cooling
|  |  | Education |  |  |  |  | 96.7%
|  |  | Grocery |  |  |  |  | 100%
|  |  | Health |  |  |  |  | 100%
|  |  | Hospital |  |  |  |  | 98.6%
|  |  | Industrial |  |  |  |  | 44.6%
|  |  | Lodging |  |  |  |  | 97.4%
|  |  | Multifamily |  |  |  |  | 100%
|  |  | Office - Large |  |  |  |  | 98.8%
|  |  | Office - Small |  |  |  |  | 100%
|  |  | Religious |  |  |  |  | 94.3%
|  |  | Restaurant |  |  |  |  | 99.6%
|  |  | Retail - Large |  |  |  |  | 87.6%
|  |  | Retail - Small |  |  |  |  | 100%
|  |  | Warehouse |  |  |  |  | 77.9%
|  |  | Nonresidential Average |  |  |  |  | 92.3%

## PTAC
PTAC
| Measure Code: | NR-HVC-PTAC-V02-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
|  |  | 8 |  |  |  |  | 3
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
|  |  | $84 per ton | $1047 per ton |  |  |  | $1039 per ton
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [([Capacity_Cool] * (1 / [EER_base] - 1 / [EER_ee ])) / [1000]] * [CF]
| Time of Sale Demand (ΔkW) | = [([Capacity_Cool] * (1 / [EER_base] - 1 / [EER_ee ])) / [1000]] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh) | = [Annual kWh Savingscool]
| Existing Unit Life Demand (ΔkW) | = [([Capacity_Cool] * (1 / [EER_exist] - 1 / [EER_ee ])) / [1000]] * [CF]
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
| Remaining Life Energy (ΔkWh) | = [Annual kWh Savingscool]
| Remaining Life Demand (ΔkW) | = [([Capacity_Cool] * (1 / [EER_base] - 1 / [EER_ee ])) / [1000]] * [CF]
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [EERbase] | Program Type | New Construction | = 14.0 – (0.300 * [Capacity_Cool]/1000)
|  |  | Replacements | = 10.9 – (0.213 * [Capacity_Cool]/1000)
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [EFLHCool] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1073 | N | Hours | Equivalent Full Load Hours for cooling
[5 empty] | Grocery |  |  | 320
[5 empty] | Health |  |  | 1449
[5 empty] | Hospital |  |  | 1792
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1472
[5 empty] | Office - Large |  |  | 1141
[5 empty] | Office - Small |  |  | 986
[5 empty] | Restaurant |  |  | 1397
[5 empty] | Retail - Large |  |  | 846
[5 empty] | Retail - Small |  |  | 891
[5 empty] | Warehouse |  |  | 1032
[5 empty] | Convenience |  |  | 1477
[5 empty] | Industrial |  |  | 1185
[5 empty] | Religious |  |  | 1109
[5 empty] | Nonresidential Average |  |  | 1034
[5 empty] | Education |  | Zone 6 (Mason City) | 848
[5 empty] | Grocery |  |  | 221
[5 empty] | Health |  |  | 996
[5 empty] | Hospital |  |  | 1436
[5 empty] | Lodging |  |  | 1252
[5 empty] | Multifamily |  |  | 1045
[5 empty] | Office - Large |  |  | 843
[5 empty] | Office - Small |  |  | 667
[5 empty] | Restaurant |  |  | 937
[5 empty] | Retail - Large |  |  | 616
[5 empty] | Retail - Small |  |  | 531
[5 empty] | Warehouse |  |  | 539
[5 empty] | Convenience |  |  | 1128
[5 empty] | Industrial |  |  | 856
[5 empty] | Religious |  |  | 797
[5 empty] | Nonresidential Average |  |  | 669
[5 empty] | Education |  | Average/Unknown | 928
[5 empty] | Grocery |  |  | 356
[5 empty] | Health |  |  | 1207
[5 empty] | Hospital |  |  | 1662
[5 empty] | Lodging |  |  | 1460
[5 empty] | Multifamily |  |  | 1349
[5 empty] | Office - Large |  |  | 1084
[5 empty] | Office - Small |  |  | 882
[5 empty] | Restaurant |  |  | 1249
[5 empty] | Retail - Large |  |  | 845
[5 empty] | Retail - Small |  |  | 780
[5 empty] | Warehouse |  |  | 864
[5 empty] | Convenience |  |  | 1351
[5 empty] | Industrial |  |  | 1063
[5 empty] | Religious |  |  | 1031
[5 empty] | Nonresidential Average |  |  | 915
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 776
[5 empty] | Health |  |  | 1482
[5 empty] | Hospital |  |  | 1422
[5 empty] | Lodging |  |  | 1204
[5 empty] | Office - Large |  |  | 816
[5 empty] | Office - Small |  |  | 616
[5 empty] | Restaurant |  |  | 915
[5 empty] | Retail - Large |  |  | 764
[5 empty] | Retail - Small |  |  | 749
[5 empty] | Warehouse |  |  | 223
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 560
[5 empty] | Education |  | Zone 6 (Mason City) | 464
[5 empty] | Health |  |  | 1073
[5 empty] | Hospital |  |  | 946
[5 empty] | Lodging |  |  | 813
[5 empty] | Office - Large |  |  | 641
[5 empty] | Office - Small |  |  | 448
[5 empty] | Restaurant |  |  | 572
[5 empty] | Retail - Large |  |  | 504
[5 empty] | Retail - Small |  |  | 486
[5 empty] | Warehouse |  |  | 35
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 338
[5 empty] | Education |  | Average/Unknown | 645
[5 empty] | Health |  |  | 1328
[5 empty] | Hospital |  |  | 1356
[5 empty] | Lodging |  |  | 1105
[5 empty] | Office - Large |  |  | 823
[5 empty] | Office - Small |  |  | 542
[5 empty] | Restaurant |  |  | 825
[5 empty] | Retail - Large |  |  | 711
[5 empty] | Retail - Small |  |  | 744
[5 empty] | Warehouse |  |  | 148
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 488
| [CapacityCool] | [7 empty] | Y | Btu/hr | Cooling Capacity of Air Source Heat Pump (Btu/hr), where 1 ton = 12000 Btu/hr
| [EERbase] | [7 empty] | C | EER | Energy Efficiency Ratio of the baseline equipment
| [EERee] | [7 empty] | Y | EER | Energy Efficiency Ratio of the energy efficient equipment
| [EERexist] | [6 empty] | 8.1 | Y | EER | Energy Efficiency Ratio of the existing equipment
| [CF] | Building Type | Convenience |  |  |  |  | 92.3% | N |  | Summer Peak Coincidence Factor for Cooling
|  |  | Education |  |  |  |  | 96.7%
|  |  | Grocery |  |  |  |  | 100%
|  |  | Health |  |  |  |  | 100%
|  |  | Hospital |  |  |  |  | 98.6%
|  |  | Industrial |  |  |  |  | 44.6%
|  |  | Lodging |  |  |  |  | 97.4%
|  |  | Multifamily |  |  |  |  | 100%
|  |  | Office - Large |  |  |  |  | 98.8%
|  |  | Office - Small |  |  |  |  | 100%
|  |  | Religious |  |  |  |  | 94.3%
|  |  | Restaurant |  |  |  |  | 99.6%
|  |  | Retail - Large |  |  |  |  | 87.6%
|  |  | Retail - Small |  |  |  |  | 100%
|  |  | Warehouse |  |  |  |  | 77.9%
|  |  | Nonresidential Average |  |  |  |  | 92.3%

## PTHP
PTHP
| Measure Code: | NR-HVC-PTAC-V02-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
|  |  | 8 |  |  |  |  | 3
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
|  |  | $84 per ton | $1047 per ton |  |  |  | $1039 per ton
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [([EFLH_cool] * [Capacity_Cool] *(1 / [EER_base] - 1 / [EER_ee] )) / [1000]] + [([EFLH_Heat] * [Capacity_Heat]* (1 / [COP_base] - 1 / ([COP_ee] ))) / [3412]]
| Time of Sale Demand (ΔkW) | = [([Capacity_Cool] * (1 / [EER_base] - 1 / [EER_ee ])) / [1000]] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh) | = [([EFLH_cool] * [Capacity_Cool] *(1 / [EER_exist] - 1 / [EER_ee] )) / [1000]] + [([EFLH_Heat] * [Capacity_Heat]* (1 / [COP_exist] - 1 / ([COP_ee] ))) / [3412]]
| Existing Unit Life Demand (ΔkW) | = [([Capacity_Cool] * (1 / [EER_exist] - 1 / [EER_ee ])) / [1000]] * [CF]
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
| Remaining Life Energy (ΔkWh) | = [([EFLH_cool] * [Capacity_Cool] *(1 / [EER_base] - 1 / [EER_ee] )) / [1000]] + [([EFLH_Heat] * [Capacity_Heat]* (1 / [COP_base] - 1 / ([COP_ee] ))) / [3412]]
| Remaining Life Demand (ΔkW) | = [([Capacity_Cool] * (1 / [EER_base] - 1 / [EER_ee ])) / [1000]] * [CF]
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [EER_base] | Program Type | New Construction | = 14.0 – (0.300 * [Capacity_Cool]/1000)
|  |  | Replacements | = 10.8 – (0.213 * [Capacity_Cool]/1000)
| [COP_base] | Program Type | New Construction | = 3.7 – (0.052 * [Capacity_Heat]/1000)
|  |  | Replacements | = 2.9 – (0.026 * [Capacity_Heat]/1000)
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [EFLHCool] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1073 | N | Hours | Equivalent Full Load Hours for cooling
[5 empty] | Grocery |  |  | 320
[5 empty] | Health |  |  | 1449
[5 empty] | Hospital |  |  | 1792
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1472
[5 empty] | Office - Large |  |  | 1141
[5 empty] | Office - Small |  |  | 986
[5 empty] | Restaurant |  |  | 1397
[5 empty] | Retail - Large |  |  | 846
[5 empty] | Retail - Small |  |  | 891
[5 empty] | Warehouse |  |  | 1032
[5 empty] | Convenience |  |  | 1477
[5 empty] | Industrial |  |  | 1185
[5 empty] | Religious |  |  | 1109
[5 empty] | Nonresidential Average |  |  | 1034
[5 empty] | Education |  | Zone 6 (Mason City) | 848
[5 empty] | Grocery |  |  | 221
[5 empty] | Health |  |  | 996
[5 empty] | Hospital |  |  | 1436
[5 empty] | Lodging |  |  | 1252
[5 empty] | Multifamily |  |  | 1045
[5 empty] | Office - Large |  |  | 843
[5 empty] | Office - Small |  |  | 667
[5 empty] | Restaurant |  |  | 937
[5 empty] | Retail - Large |  |  | 616
[5 empty] | Retail - Small |  |  | 531
[5 empty] | Warehouse |  |  | 539
[5 empty] | Convenience |  |  | 1128
[5 empty] | Industrial |  |  | 856
[5 empty] | Religious |  |  | 797
[5 empty] | Nonresidential Average |  |  | 669
[5 empty] | Education |  | Average/Unknown | 928
[5 empty] | Grocery |  |  | 356
[5 empty] | Health |  |  | 1207
[5 empty] | Hospital |  |  | 1662
[5 empty] | Lodging |  |  | 1460
[5 empty] | Multifamily |  |  | 1349
[5 empty] | Office - Large |  |  | 1084
[5 empty] | Office - Small |  |  | 882
[5 empty] | Restaurant |  |  | 1249
[5 empty] | Retail - Large |  |  | 845
[5 empty] | Retail - Small |  |  | 780
[5 empty] | Warehouse |  |  | 864
[5 empty] | Convenience |  |  | 1351
[5 empty] | Industrial |  |  | 1063
[5 empty] | Religious |  |  | 1031
[5 empty] | Nonresidential Average |  |  | 915
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 776
[5 empty] | Health |  |  | 1482
[5 empty] | Hospital |  |  | 1422
[5 empty] | Lodging |  |  | 1204
[5 empty] | Office - Large |  |  | 816
[5 empty] | Office - Small |  |  | 616
[5 empty] | Restaurant |  |  | 915
[5 empty] | Retail - Large |  |  | 764
[5 empty] | Retail - Small |  |  | 749
[5 empty] | Warehouse |  |  | 223
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 560
[5 empty] | Education |  | Zone 6 (Mason City) | 464
[5 empty] | Health |  |  | 1073
[5 empty] | Hospital |  |  | 946
[5 empty] | Lodging |  |  | 813
[5 empty] | Office - Large |  |  | 641
[5 empty] | Office - Small |  |  | 448
[5 empty] | Restaurant |  |  | 572
[5 empty] | Retail - Large |  |  | 504
[5 empty] | Retail - Small |  |  | 486
[5 empty] | Warehouse |  |  | 35
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 338
[5 empty] | Education |  | Average/Unknown | 645
[5 empty] | Health |  |  | 1328
[5 empty] | Hospital |  |  | 1356
[5 empty] | Lodging |  |  | 1105
[5 empty] | Office - Large |  |  | 823
[5 empty] | Office - Small |  |  | 542
[5 empty] | Restaurant |  |  | 825
[5 empty] | Retail - Large |  |  | 711
[5 empty] | Retail - Small |  |  | 744
[5 empty] | Warehouse |  |  | 148
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 488
| [CapacityCool] | [7 empty] | Y | Btu/hr | Cooling Capacity of Air Source Heat Pump (Btu/hr), where 1 ton = 12000 Btu/hr
| [EER_base] | [7 empty] | C | EER | Energy Efficiency Ratio of the baseline equipment
| [EER_ee] | [7 empty] | Y |  | Energy efficiency Ratio of the energy efficient equipment
| [EER_exist] | [6 empty] | 8.1 | Y |  | Energy efficiency ration of existing equipment
| [EFLHHeat] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1298 | N | Hours | Equivalent Full Load Hours for heating space
[5 empty] | Grocery |  |  | 1493
[5 empty] | Health |  |  | 1206
[5 empty] | Hospital |  |  | 1084
[5 empty] | Lodging |  |  | 1365
[5 empty] | Multifamily |  |  | 1521
[5 empty] | Office - Large |  |  | 1457
[5 empty] | Office - Small |  |  | 1250
[5 empty] | Restaurant |  |  | 1040
[5 empty] | Retail - Large |  |  | 1255
[5 empty] | Retail - Small |  |  | 1172
[5 empty] | Warehouse |  |  | 1277
[5 empty] | Convenience |  |  | 785
[5 empty] | Industrial |  |  | 849
[5 empty] | Religious |  |  | 1322
[5 empty] | Nonresidential Average |  |  | 1251
[5 empty] | Education |  | Zone 6 (Mason City) | 1529
[5 empty] | Grocery |  |  | 1754
[5 empty] | Health |  |  | 1430
[5 empty] | Hospital |  |  | 940
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1846
[5 empty] | Office - Large |  |  | 1748
[5 empty] | Office - Small |  |  | 1435
[5 empty] | Restaurant |  |  | 1324
[5 empty] | Retail - Large |  |  | 1523
[5 empty] | Retail - Small |  |  | 1471
[5 empty] | Warehouse |  |  | 1589
[5 empty] | Convenience |  |  | 1224
[5 empty] | Industrial |  |  | 1275
[5 empty] | Religious |  |  | 1873
[5 empty] | Nonresidential Average |  |  | 1555
[5 empty] | Education |  | Average/Unknown | 1351
[5 empty] | Grocery |  |  | 1601
[5 empty] | Health |  |  | 1346
[5 empty] | Hospital |  |  | 1082
[5 empty] | Lodging |  |  | 1494
[5 empty] | Multifamily |  |  | 1694
[5 empty] | Office - Large |  |  | 1549
[5 empty] | Office - Small |  |  | 1358
[5 empty] | Restaurant |  |  | 1173
[5 empty] | Retail - Large |  |  | 1348
[5 empty] | Retail - Small |  |  | 1372
[5 empty] | Warehouse |  |  | 1443
[5 empty] | Convenience |  |  | 1071
[5 empty] | Industrial |  |  | 1183
[5 empty] | Religious |  |  | 1796
[5 empty] | Nonresidential Average |  |  | 1438
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 510
[5 empty] | Health |  |  | 778
[5 empty] | Hospital |  |  | 1799
[5 empty] | Lodging |  |  | 1080
[5 empty] | Office - Large |  |  | 710
[5 empty] | Office - Small |  |  | 450
[5 empty] | Restaurant |  |  | 896
[5 empty] | Retail - Large |  |  | 709
[5 empty] | Retail - Small |  |  | 785
[5 empty] | Warehouse |  |  | 886
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 690
[5 empty] | Education |  | Zone 6 (Mason City) | 683
[5 empty] | Health |  |  | 972
[5 empty] | Hospital |  |  | 1520
[5 empty] | Lodging |  |  | 1491
[5 empty] | Office - Large |  |  | 917
[5 empty] | Office - Small |  |  | 590
[5 empty] | Restaurant |  |  | 1192
[5 empty] | Retail - Large |  |  | 906
[5 empty] | Retail - Small |  |  | 1036
[5 empty] | Warehouse |  |  | 1238
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 930
[5 empty] | Education |  | Average/Unknown | 591
[5 empty] | Health |  |  | 864
[5 empty] | Hospital |  |  | 2196
[5 empty] | Lodging |  |  | 1471
[5 empty] | Office - Large |  |  | 862
[5 empty] | Office - Small |  |  | 492
[5 empty] | Restaurant |  |  | 1048
[5 empty] | Retail - Large |  |  | 839
[5 empty] | Retail - Small |  |  | 986
[5 empty] | Warehouse |  |  | 1116
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 830
| [CapacityHeat] | [7 empty] | Y | Btu/hr | Heating Capacity of Air Source Heat Pump (Btu/hr), where 1 ton = 12000 Btu/hr
| [COP_base] | [7 empty] | C |  | coefficient of performance of the baseline equipment
| [COP_ee] | [7 empty] | Y |  | Coefficient of performance of the energy efficient equipment
| [COP_exist] | [6 empty] | 2.6 | Y |  | Coefficient of performance of the existing equipment
| [3,412] | [6 empty] | 3412 | N | kBtu/kWh | kBtu/kWh
| [CF] | Building Type | Convenience |  |  |  |  | 92.3% | N |  | Summer Peak Coincidence Factor for Cooling
|  |  | Education |  |  |  |  | 96.7%
|  |  | Grocery |  |  |  |  | 100%
|  |  | Health |  |  |  |  | 100%
|  |  | Hospital |  |  |  |  | 98.6%
|  |  | Industrial |  |  |  |  | 44.6%
|  |  | Lodging |  |  |  |  | 97.4%
|  |  | Multifamily |  |  |  |  | 100%
|  |  | Office - Large |  |  |  |  | 98.8%
|  |  | Office - Small |  |  |  |  | 100%
|  |  | Religious |  |  |  |  | 94.3%
|  |  | Restaurant |  |  |  |  | 99.6%
|  |  | Retail - Large |  |  |  |  | 87.6%
|  |  | Retail - Small |  |  |  |  | 100%
|  |  | Warehouse |  |  |  |  | 77.9%
|  |  | Nonresidential Average |  |  |  |  | 92.3%

## Guest Room Energy Mgmt (PTAC)
Guest Room Energy Mgmt (PTAC)
| Measure Code: | NR-HVC-GREM-V02-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
260
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [Rooms] *([Heating savings] + [Cooling savings] + [Lighting savings])
| Time of Sale Demand (ΔkW) | = [Rooms] * ([Cooling savings])/ [EFLH_Cool] * [CF]
| Time of Sale Gas (ΔTherms) | = [Rooms]* [Gas Savings]
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Rooms] | [7 empty] | Y |  | Number of rooms with a GREM system installed
| [Heating savings] | Climate Zone | Zone 5 (Burlington) |  |  |  |  | 111.3 | N | kWh/room/year | Heating kWh Savings
|  |  | Zone 6 (Mason City) |  |  |  |  | 151.5
|  |  | Average/Unknown |  |  |  |  | 135.8
| [Cooling savings] | Climate Zone | Zone 5 (Burlington) |  |  |  |  | 24.6 | N | kWh/room/year | Cooling kWh Savings
|  |  | Zone 6 (Mason City) |  |  |  |  | 17.8
|  |  | Average/Unknown |  |  |  |  | 22.2
| [Lighting savings] | Climate Zone | Zone 5 (Burlington) |  |  |  |  | 62 | N | kWh/room/year | Lighting kWh Savings
|  |  | Zone 6 (Mason City) |  |  |  |  | 62
|  |  | Average/Unknown |  |  |  |  | 62
| [EFLHCool] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1073 | N | Hours | Equivalent Full Load Hours for cooling
[5 empty] | Grocery |  |  | 320
[5 empty] | Health |  |  | 1449
[5 empty] | Hospital |  |  | 1792
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1472
[5 empty] | Office - Large |  |  | 1141
[5 empty] | Office - Small |  |  | 986
[5 empty] | Restaurant |  |  | 1397
[5 empty] | Retail - Large |  |  | 846
[5 empty] | Retail - Small |  |  | 891
[5 empty] | Warehouse |  |  | 1032
[5 empty] | Convenience |  |  | 1477
[5 empty] | Industrial |  |  | 1185
[5 empty] | Religious |  |  | 1109
[5 empty] | Nonresidential Average |  |  | 1034
[5 empty] | Education |  | Zone 6 (Mason City) | 848
[5 empty] | Grocery |  |  | 221
[5 empty] | Health |  |  | 996
[5 empty] | Hospital |  |  | 1436
[5 empty] | Lodging |  |  | 1252
[5 empty] | Multifamily |  |  | 1045
[5 empty] | Office - Large |  |  | 843
[5 empty] | Office - Small |  |  | 667
[5 empty] | Restaurant |  |  | 937
[5 empty] | Retail - Large |  |  | 616
[5 empty] | Retail - Small |  |  | 531
[5 empty] | Warehouse |  |  | 539
[5 empty] | Convenience |  |  | 1128
[5 empty] | Industrial |  |  | 856
[5 empty] | Religious |  |  | 797
[5 empty] | Nonresidential Average |  |  | 669
[5 empty] | Education |  | Average/Unknown | 928
[5 empty] | Grocery |  |  | 356
[5 empty] | Health |  |  | 1207
[5 empty] | Hospital |  |  | 1662
[5 empty] | Lodging |  |  | 1460
[5 empty] | Multifamily |  |  | 1349
[5 empty] | Office - Large |  |  | 1084
[5 empty] | Office - Small |  |  | 882
[5 empty] | Restaurant |  |  | 1249
[5 empty] | Retail - Large |  |  | 845
[5 empty] | Retail - Small |  |  | 780
[5 empty] | Warehouse |  |  | 864
[5 empty] | Convenience |  |  | 1351
[5 empty] | Industrial |  |  | 1063
[5 empty] | Religious |  |  | 1031
[5 empty] | Nonresidential Average |  |  | 915
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 776
[5 empty] | Health |  |  | 1482
[5 empty] | Hospital |  |  | 1422
[5 empty] | Lodging |  |  | 1204
[5 empty] | Office - Large |  |  | 816
[5 empty] | Office - Small |  |  | 616
[5 empty] | Restaurant |  |  | 915
[5 empty] | Retail - Large |  |  | 764
[5 empty] | Retail - Small |  |  | 749
[5 empty] | Warehouse |  |  | 223
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 560
[5 empty] | Education |  | Zone 6 (Mason City) | 464
[5 empty] | Health |  |  | 1073
[5 empty] | Hospital |  |  | 946
[5 empty] | Lodging |  |  | 813
[5 empty] | Office - Large |  |  | 641
[5 empty] | Office - Small |  |  | 448
[5 empty] | Restaurant |  |  | 572
[5 empty] | Retail - Large |  |  | 504
[5 empty] | Retail - Small |  |  | 486
[5 empty] | Warehouse |  |  | 35
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 338
[5 empty] | Education |  | Average/Unknown | 645
[5 empty] | Health |  |  | 1328
[5 empty] | Hospital |  |  | 1356
[5 empty] | Lodging |  |  | 1105
[5 empty] | Office - Large |  |  | 823
[5 empty] | Office - Small |  |  | 542
[5 empty] | Restaurant |  |  | 825
[5 empty] | Retail - Large |  |  | 711
[5 empty] | Retail - Small |  |  | 744
[5 empty] | Warehouse |  |  | 148
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 488
| [CF] | [6 empty] | 97.4% | N |  | Summer System Peak Coincidence Factor for cooling
| [Gas Savings] | Climate Zone | Zone 5 (Burlington) |  |  |  |  | 4.7 | N | therms/room/year | Gas savings factor
|  |  | Zone 6 (Mason City) |  |  |  |  | 6.5
|  |  | Average/Unknown |  |  |  |  | 5.8
| [Δtherms] | [7 empty] | N | therms | Therm impact calcualted above
| [GCF] | [6 empty] | 0.68194 | N |  | Gas Coincidence Factor for Heating

## Boiler Tune Up
Boiler Tune Up
| Measure Code: | NR-HVC-BLRT-V02-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
1
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | = ([Capacity] * [EFLH ]*((([Effbefore] + [Ei])) / [Effbefore] – 1)) / [100,000]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Capacity] | [7 empty] | Y | Btu/hr | Gas Boiler input size
| [EFLHHeat] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1298 | N | Hours | Equivalent Full Load Hours for heating space
[5 empty] | Grocery |  |  | 1493
[5 empty] | Health |  |  | 1206
[5 empty] | Hospital |  |  | 1084
[5 empty] | Lodging |  |  | 1365
[5 empty] | Multifamily |  |  | 1521
[5 empty] | Office - Large |  |  | 1457
[5 empty] | Office - Small |  |  | 1250
[5 empty] | Restaurant |  |  | 1040
[5 empty] | Retail - Large |  |  | 1255
[5 empty] | Retail - Small |  |  | 1172
[5 empty] | Warehouse |  |  | 1277
[5 empty] | Convenience |  |  | 785
[5 empty] | Industrial |  |  | 849
[5 empty] | Religious |  |  | 1322
[5 empty] | Nonresidential Average |  |  | 1251
[5 empty] | Education |  | Zone 6 (Mason City) | 1529
[5 empty] | Grocery |  |  | 1754
[5 empty] | Health |  |  | 1430
[5 empty] | Hospital |  |  | 940
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1846
[5 empty] | Office - Large |  |  | 1748
[5 empty] | Office - Small |  |  | 1435
[5 empty] | Restaurant |  |  | 1324
[5 empty] | Retail - Large |  |  | 1523
[5 empty] | Retail - Small |  |  | 1471
[5 empty] | Warehouse |  |  | 1589
[5 empty] | Convenience |  |  | 1224
[5 empty] | Industrial |  |  | 1275
[5 empty] | Religious |  |  | 1873
[5 empty] | Nonresidential Average |  |  | 1555
[5 empty] | Education |  | Average/Unknown | 1351
[5 empty] | Grocery |  |  | 1601
[5 empty] | Health |  |  | 1346
[5 empty] | Hospital |  |  | 1082
[5 empty] | Lodging |  |  | 1494
[5 empty] | Multifamily |  |  | 1694
[5 empty] | Office - Large |  |  | 1549
[5 empty] | Office - Small |  |  | 1358
[5 empty] | Restaurant |  |  | 1173
[5 empty] | Retail - Large |  |  | 1348
[5 empty] | Retail - Small |  |  | 1372
[5 empty] | Warehouse |  |  | 1443
[5 empty] | Convenience |  |  | 1071
[5 empty] | Industrial |  |  | 1183
[5 empty] | Religious |  |  | 1796
[5 empty] | Nonresidential Average |  |  | 1438
| [Effbefore] | [7 empty] | Y |  | Combustion Efficiency of the boiler before the tune-up
| [Ei] | [7 empty] | Y |  | Combustion Efficiency Improvement of the boiler tune-up measure
| [100,000] | [6 empty] | 100000 | N | Btu/Therm | Converts Btus to Therms
| [ΔTherms] | [7 empty] | C | therm | Therm impact calculated above
| [GCF] | Building Type | Convenience |  |  |  |  | 0.01631 | N | GCF | Gas Coincidence Factor for Heating
|  |  | Education |  |  |  |  | 0.01148
|  |  | Grocery |  |  |  |  | 0.013083
|  |  | Health |  |  |  |  | 0.010179
|  |  | Hospital |  |  |  |  | 0.015543
|  |  | Industrial |  |  |  |  | 0.01424
|  |  | Lodging |  |  |  |  | 0.013205
|  |  | Multifamily |  |  |  |  | 0.012268
|  |  | Office - Large |  |  |  |  | 0.013082
|  |  | Office - Small |  |  |  |  | 0.016718
|  |  | Religious |  |  |  |  | 0.011745
|  |  | Restaurant |  |  |  |  | 0.015262
|  |  | Retail - Large |  |  |  |  | 0.013281
|  |  | Retail - Small |  |  |  |  | 0.014055
|  |  | Warehouse |  |  |  |  | 0.015677
|  |  | Nonresidential Average |  |  |  |  | 0.014623

## Furnace Tune Up
Furnace Tune Up
| Measure Code: | NR-HVC-FTUN-V03-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
2
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [ΔTherms] * [Fe] * [29.3]
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | = ([Capacity] * [EFLH] * ((([Effbefore] + [Ei])) / [Effbefore] – 1) ) / [100,000]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [ΔTherms] | [7 empty] | C | therm | As calculated below
| [Fe] | [6 empty] | 3.14% | N |  | Furnace Fan energy consumption as a percentage of annual fuel consumption
| [29.3] | [6 empty] | 29.3 | N | kWh/therm | kWh per therm
| [Capacity] | [7 empty] | Y | Btu/hr | Nominal heating input capacity furnace size (Btu/hr)
| [EFLHHeat] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1298 | N | Hours | Equivalent Full Load Hours for heating space
[5 empty] | Grocery |  |  | 1493
[5 empty] | Health |  |  | 1206
[5 empty] | Hospital |  |  | 1084
[5 empty] | Lodging |  |  | 1365
[5 empty] | Multifamily |  |  | 1521
[5 empty] | Office - Large |  |  | 1457
[5 empty] | Office - Small |  |  | 1250
[5 empty] | Restaurant |  |  | 1040
[5 empty] | Retail - Large |  |  | 1255
[5 empty] | Retail - Small |  |  | 1172
[5 empty] | Warehouse |  |  | 1277
[5 empty] | Convenience |  |  | 785
[5 empty] | Industrial |  |  | 849
[5 empty] | Religious |  |  | 1322
[5 empty] | Nonresidential Average |  |  | 1251
[5 empty] | Education |  | Zone 6 (Mason City) | 1529
[5 empty] | Grocery |  |  | 1754
[5 empty] | Health |  |  | 1430
[5 empty] | Hospital |  |  | 940
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1846
[5 empty] | Office - Large |  |  | 1748
[5 empty] | Office - Small |  |  | 1435
[5 empty] | Restaurant |  |  | 1324
[5 empty] | Retail - Large |  |  | 1523
[5 empty] | Retail - Small |  |  | 1471
[5 empty] | Warehouse |  |  | 1589
[5 empty] | Convenience |  |  | 1224
[5 empty] | Industrial |  |  | 1275
[5 empty] | Religious |  |  | 1873
[5 empty] | Nonresidential Average |  |  | 1555
[5 empty] | Education |  | Average/Unknown | 1351
[5 empty] | Grocery |  |  | 1601
[5 empty] | Health |  |  | 1346
[5 empty] | Hospital |  |  | 1082
[5 empty] | Lodging |  |  | 1494
[5 empty] | Multifamily |  |  | 1694
[5 empty] | Office - Large |  |  | 1549
[5 empty] | Office - Small |  |  | 1358
[5 empty] | Restaurant |  |  | 1173
[5 empty] | Retail - Large |  |  | 1348
[5 empty] | Retail - Small |  |  | 1372
[5 empty] | Warehouse |  |  | 1443
[5 empty] | Convenience |  |  | 1071
[5 empty] | Industrial |  |  | 1183
[5 empty] | Religious |  |  | 1796
[5 empty] | Nonresidential Average |  |  | 1438
| [Effbefore] | [7 empty] | Y |  | Combustion Efficiency of the boiler before the tune-up
| [Ei] | [7 empty] | Y |  | Combustion Efficiency Improvement of the boiler tune-up measure
| [100,000] | [6 empty] | 100000 | N | Btu/Therm | Converts Btus to Therms
| [ΔTherms] | [7 empty] | C | therm | Therm impact calculated above
| [GCF] |  |  | Building Type | Convenience |  |  | 0.016482 | N | GCF | Gas Coincidence Factor for Heating
[5 empty] | Education |  |  | 0.01148
[5 empty] | Grocery |  |  | 0.013083
[5 empty] | Health |  |  | 0.010179
[5 empty] | Hospital |  |  | 0.015543
[5 empty] | Industrial |  |  | 0.01424
[5 empty] | Lodging |  |  | 0.013205
[5 empty] | Multifamily |  |  | 0.012268
[5 empty] | Office - Large |  |  | 0.013082
[5 empty] | Office - Small |  |  | 0.016718
[5 empty] | Religious |  |  | 0.011964
[5 empty] | Restaurant |  |  | 0.015262
[5 empty] | Retail - Large |  |  | 0.013281
[5 empty] | Retail - Small |  |  | 0.014055
[5 empty] | Warehouse |  |  | 0.015677
[5 empty] | Nonresidential Average |  |  | 0.014658

## Sm. Commercial Thermostat
Sm. Commercial Thermostat
| Measure Code: | NR-HVC-PROG-V04-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
8
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Labor cost of implementation | Known | Actual
|  | Unknown | 181
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [∆kWh_cooling] + [∆kWh_heating]
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | = ([Sqft] * [Savings Factor_heat])/(100 * [EfficiencyRating(exist)_heat])
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [∆kWh_cooling] |  |  | = ([Sqft] * [Savings Factor_cool]) / [EfficiencyRating(exist)_cool]
| [∆kWh_heating] |  |  | = ([Sqft] * [Savings Factor_heat]) / ([3.412] * [EfficiencyRating(exist)_electric heat])
| [∆kWh_heating] |  |  | = [ΔTherms] * [Fe] * [29.3]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Sqft] | [5 empty] | Y | ft2 | Square footage of building controlled by thermostat
| [EfficiencyRating(exist)_cool] | [5 empty] | Y | btuhr/w | Efficiency rating of existing cooling equipment EER (btu hr/w)
| [Savings Factor_cool] |  |  |  |  | 0.53 | N | kBtu/sf-yr | Savings factor for cooling
| [Savings Factor_heat] |  |  |  |  | 0.85 | N | kBtu/sf-yr | Savings factor for heating
| [3.412] |  |  |  |  | 3.412 | N |  | Conversion from kBtu to kWh
| [EfficiencyRating(exist)_electric heat] | [5 empty] | Y |  | Efficiency rating of existing heating equipment EER (AFUE)
| [ΔTherms] | [5 empty] | C | therm | Therm impact
| [Fe] |  |  |  |  | 3.14% | N |  | Percentage of heating energy consumed by fans
| [29.3] |  |  |  |  | 29.3 | N |  | Conversion from therms to kWh
| [EfficiencyRating(exist)_heat] | [5 empty] | Y |  | Efficiency rating of existing heating equipment (AFUE)
| [GCF] | Building Type | Convenience |  |  | 0.016482 | N | GCF | Gas Coincidence Factor for Heating
|  |  | Education |  |  | 0.01148
|  |  | Grocery |  |  | 0.013083
|  |  | Health |  |  | 0.010179
|  |  | Hospital |  |  | 0.015543
|  |  | Industrial |  |  | 0.014296
|  |  | Lodging |  |  | 0.013205
|  |  | Multifamily |  |  | 0.012268
|  |  | Office - Large |  |  | 0.013082
|  |  | Office - Small |  |  | 0.016718
|  |  | Religious |  |  | 0.011964
|  |  | Restaurant |  |  | 0.015262
|  |  | Retail - Large |  |  | 0.013281
|  |  | Retail - Small |  |  | 0.014055
|  |  | Warehouse |  |  | 0.015677
|  |  | Nonresidential Average |  |  | 0.014658

## VFDs for HVAC Pumps
VFDs for HVAC Pumps
| Measure Code: | NR-HVC-VFHP-V04-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Costs known? | Known |  |  | Actual
|  | Unknown | Horse Power | 1-9 | 2177
|  |  |  | 10-19 | 3123
|  |  |  | 20-29 | 4280
|  |  |  | 30-39 | 5023
|  |  |  | 40-49 | 5766
|  |  |  | 50-59 | 6591
|  |  |  | 60-69 | 7550
|  |  |  | 70-79 | 8173
|  |  |  | 80-89 | 8796
|  |  |  | 90-100 | 9576
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([BHP] ) / [EFFi] * [Hours] * [ESF]
| Time of Sale Demand (ΔkW) | =[BHP] / [EFFi] * [DSF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [BHP] |  |  | = ([Nominal motor HP] * [Motor load factor])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [BHP] | [5 empty] | C |  | System Brake Horsepower
| [Nominal motor HP] | [5 empty] | Y |  | Nominal motor horse power
| [Motor load factor] |  |  |  |  | 65% | Y |  | Motor load factor
| [EFFi] | [5 empty] | Y |  | Motor efficiency, installed
| [Hours] | Building Type | Convenience | Pump Type | Heating | 3628 | Y | Hours | Default hours are provided for HVAC applications which vary by building type. When available, actual hours should be used. The type of hours to apply depends on the VFD application.
|  |  | Education |  |  | 6367
|  |  | Grocery |  |  | 6499
|  |  | Health |  |  | 8720
|  |  | Hospital |  |  | 8289
|  |  | Industrial |  |  | 3977
|  |  | Lodging |  |  | 5500
|  |  | Multifamily |  |  | 5382
|  |  | Office - Large |  |  | 5316
|  |  | Office - Small |  |  | 1952
|  |  | Religious |  |  | 4763
|  |  | Restaurant |  |  | 3027
|  |  | Retail - Large |  |  | 4218
|  |  | Retail - Small |  |  | 3029
|  |  | Warehouse |  |  | 4100
|  |  | Nonresidential Average |  |  | 3659
|  |  | Convenience |  | Cooling | 2690
|  |  | Education |  |  | 2796
|  |  | Grocery |  |  | 2725
|  |  | Health |  |  | 4770
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 3080
|  |  | Lodging |  |  | 7909
|  |  | Multifamily |  |  | 5084
|  |  | Office - Large |  |  | 4596
|  |  | Office - Small |  |  | 2138
|  |  | Religious |  |  | 2223
|  |  | Restaurant |  |  | 2719
|  |  | Retail - Large |  |  | 2405
|  |  | Retail - Small |  |  | 2266
|  |  | Warehouse |  |  | 1788
|  |  | Nonresidential Average |  |  | 2182
| [ESF] | Application | Hot Water Centrifugal Pump |  |  | 0.187 | N | kW/HP | Energy savings factor varies by VFD application
|  |  | Chilled Water Centrifugal Pump |  |  | 0.094
|  |  | Cooling Tower Fan |  |  | 0.382
| [DSF] | Application | Hot Water Centrifugal Pump |  |  | 0 | N | kW/HP | Demand Savings Factor varies by VFD application. Units are kW/HP. Values listed below are based on typical peak load for the listed application
|  |  | Chilled Water Centrifugal Pump |  |  | 0
|  |  | Cooling Tower Fan |  |  | 0.32

## VFDs for HVAC Sup. and Ret. Fan
VFDs for HVAC Sup. and Ret. Fan
| Measure Code: | NR-HVC-VFDF-V03-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Costs known? | Known |  |  | Actual
|  | Unknown | Horse Power | 1-9 | 2177
|  |  |  | 10-19 | 3123
|  |  |  | 20-29 | 4280
|  |  |  | 30-39 | 5023
|  |  |  | 40-49 | 5766
|  |  |  | 50-59 | 6591
|  |  |  | 60-69 | 7550
|  |  |  | 70-79 | 8173
|  |  |  | 80-89 | 8796
|  |  |  | 90-100 | 9576
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([kWh_Base]-[kWh_Retrofit]) *(1+[IE_energy])
| Time of Sale Demand (ΔkW) | =([kW_Base]-[kW_Retrofit]) *(1+[IE_demand])
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [kWh_Base] |  |  | =([0.746]*[HP]*[LF]/[η_motor])*[RHRS_Base]*[∑(%FF*PLR_Base)]
| [kWh_Retrofit] |  |  | =([0.746]*[HP]*[LF]/[η_motor])*[RHRS_Base]*[∑(%FF*PLR_Retrofit)]
| [kW_Base] |  |  | =([0.746]*[HP]*[LF]/[η_motor])*[PLR_BaseFFPeak]
| [kW_Retrofit] |  |  | =([0.746]*[HP]*[LF]/[η_motor])*[PLR_RetrofitFFPeak]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [kWh_Base] | [5 empty] | C |  | Baseline annual energy consumption
| [kWh_Retrofit] | [5 empty] | C |  | Retrofit annual energy consumption
| [0.746] |  |  |  |  | 0.746 | N |  | Conversion factor for HP to kWh
| [HP] | [5 empty] | Y | HP | Nominal horsepower of controlled motor
| [LF] |  |  |  |  | 0.65 | Y | Percentage | Load Factor; Motor Load at Fan Design CFM
| [η_motor] | [5 empty] | Y | Percentage | Installed nominal/nameplate motor efficiency
| [RHRS_Base] | Building Type | Convenience |  |  | 4630 | Y | Hours | Annual operating hours for fan motor based on building type
|  |  | Education |  |  | 3544
|  |  | Grocery |  |  | 8743
|  |  | Health |  |  | 3478
|  |  | Hospital |  |  | 4570
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3909
|  |  | Multifamily |  |  | 8760
|  |  | Office - Large |  |  | 2662
|  |  | Office - Small |  |  | 7667
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 7300
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 7410
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 4978
| [∑(%FF*PLR_Base)] | Control Type | No Control or Bypass Damper |  |  | 1 | N |  | Sum of %FF * Part Load Ratio based on baseline flow control type
|  |  | Discharge Dampers |  |  | 0.8
|  |  | Outlet Damper, BI & Airfoil Fans |  |  | 0.78
|  |  | Inlet Damper Box |  |  | 0.69
|  |  | Inlet Guide Vane, BI & Airfoil Fans |  |  | 0.63
|  |  | Inlet Vane Dampers |  |  | 0.53
|  |  | Outlet Damper, FC Fans |  |  | 0.53
|  |  | Eddy Current Drives |  |  | 0.49
|  |  | Inlet Guide Vane, FC Fans |  |  | 0.39
|  |  | VFD with duct static pressure controls |  |  | 0.3
|  |  | VFD with low/no duct static pressure |  |  | 0.27
| [∑(%FF*PLR_Retrofit)] | Control Type | No Control or Bypass Damper |  |  | 1 | N |  | Sum of %FF * Part Load Ratio based on retrofit flow control type
|  |  | Discharge Dampers |  |  | 0.8
|  |  | Outlet Damper, BI & Airfoil Fans |  |  | 0.78
|  |  | Inlet Damper Box |  |  | 0.69
|  |  | Inlet Guide Vane, BI & Airfoil Fans |  |  | 0.63
|  |  | Inlet Vane Dampers |  |  | 0.53
|  |  | Outlet Damper, FC Fans |  |  | 0.53
|  |  | Eddy Current Drives |  |  | 0.49
|  |  | Inlet Guide Vane, FC Fans |  |  | 0.39
|  |  | VFD with duct static pressure controls |  |  | 0.3
|  |  | VFD with low/no duct static pressure |  |  | 0.27
| [IE_energy] |  |  |  |  | 0.157 | N |  | HVAC interactive effects factor for energy
| [kW_Base] | [5 empty] | C | kW | Baseline summer coincident peak demand
| [kW_Retrofit] | [5 empty] | C | kW | Retrofit summer coincident peak demand
| [PLR_BaseFFPeak] | Control Type | No Control or Bypass Damper |  |  | 1 | N |  | The part load ratio for the average flow fraction between the peak daytime hours during the weekday peak time period based on the baseline flow control type (default average flow fraction during peak period = 90%)
|  |  | Discharge Dampers |  |  | 0.97
|  |  | Outlet Damper, BI & Airfoil Fans |  |  | 1.02
|  |  | Inlet Damper Box |  |  | 0.92
|  |  | Inlet Guide Vane, BI & Airfoil Fans |  |  | 0.85
|  |  | Inlet Vane Dampers |  |  | 0.83
|  |  | Outlet Damper, FC Fans |  |  | 0.91
|  |  | Eddy Current Drives |  |  | 0.9
|  |  | Inlet Guide Vane, FC Fans |  |  | 0.81
|  |  | VFD with duct static pressure controls |  |  | 0.76
|  |  | VFD with low/no duct static pressure |  |  | 0.75
| [PLR_RetrofitFFPeak] | Control Type | No Control or Bypass Damper |  |  | 1 | N |  | The part load ratio for the average flow fraction between the peak daytime hours during the weekday peak time period based on the retrofit flow control type (default average flow fraction during peak period = 90%)
|  |  | Discharge Dampers |  |  | 0.97
|  |  | Outlet Damper, BI & Airfoil Fans |  |  | 1.02
|  |  | Inlet Damper Box |  |  | 0.92
|  |  | Inlet Guide Vane, BI & Airfoil Fans |  |  | 0.85
|  |  | Inlet Vane Dampers |  |  | 0.83
|  |  | Outlet Damper, FC Fans |  |  | 0.91
|  |  | Eddy Current Drives |  |  | 0.9
|  |  | Inlet Guide Vane, FC Fans |  |  | 0.81
|  |  | VFD with duct static pressure controls |  |  | 0.76
|  |  | VFD with low/no duct static pressure |  |  | 0.75
| [IE_demand] |  |  |  |  | 0.157 | N |  | HVAC interactive effects factor for summer coincident peak demand

## Duct Insulation
Duct Insulation
| Measure Code: | NR-HVC-DUCT-V02-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
20
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known |  | Actual
| Cost unknown |  | $1.36/ft2
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [∆kWhcooling] + [∆kWhheating]
| Time of Sale Demand (ΔkW) | = [∆kWhcooling] / [EFLHcooling] * [CF]
| Time of Sale Gas (ΔTherms) | = ((1 / [R_existing] - 1 / [R_new] ) * [Area] * [EFLH_heating] * [∆T_AVG,heating] / (([100,000] * [η_heat]))
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [∆kWh_cooling] |  |  | = ((1 / [R_existing] - 1 / [R_new ]) * [Area] * [EFLH_cooling] * ][T_AVG,cooling] / (([1,000 ] * [η_cooling]))
| [∆kWh_heating] | Heating Type | Electric | = ((1 / [R_existing] - 1 / [R_new] ) * [Area] * [EFLH_heating] * [∆T_AVG,heating] / (([3,412] * [η_heating]))
|  |  | Gas | = [∆Therms] * [Fe] * [29.3]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Rexisting] | [7 empty] | Y | (hr-⁰F-ft2)/Btu | Duct heat loss coefficient with existing insulation
| [Rnew] | [7 empty] | Y | (hr-⁰F-ft2)/Btu | Duct heat loss coefficient with new insulation
| [Area] | [7 empty] | Y | ft2 | Area of the duct surface exposed to the unconditioned space that has been insulated
| [EFLHCool] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1073 | N | Hours | Equivalent Full Load Hours for cooling
[5 empty] | Grocery |  |  | 320
[5 empty] | Health |  |  | 1449
[5 empty] | Hospital |  |  | 1792
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1472
[5 empty] | Office - Large |  |  | 1141
[5 empty] | Office - Small |  |  | 986
[5 empty] | Restaurant |  |  | 1397
[5 empty] | Retail - Large |  |  | 846
[5 empty] | Retail - Small |  |  | 891
[5 empty] | Warehouse |  |  | 1032
[5 empty] | Convenience |  |  | 1477
[5 empty] | Industrial |  |  | 1185
[5 empty] | Religious |  |  | 1109
[5 empty] | Nonresidential Average |  |  | 1034
[5 empty] | Education |  | Zone 6 (Mason City) | 848
[5 empty] | Grocery |  |  | 221
[5 empty] | Health |  |  | 996
[5 empty] | Hospital |  |  | 1436
[5 empty] | Lodging |  |  | 1252
[5 empty] | Multifamily |  |  | 1045
[5 empty] | Office - Large |  |  | 843
[5 empty] | Office - Small |  |  | 667
[5 empty] | Restaurant |  |  | 937
[5 empty] | Retail - Large |  |  | 616
[5 empty] | Retail - Small |  |  | 531
[5 empty] | Warehouse |  |  | 539
[5 empty] | Convenience |  |  | 1128
[5 empty] | Industrial |  |  | 856
[5 empty] | Religious |  |  | 797
[5 empty] | Nonresidential Average |  |  | 669
[5 empty] | Education |  | Average/Unknown | 928
[5 empty] | Grocery |  |  | 356
[5 empty] | Health |  |  | 1207
[5 empty] | Hospital |  |  | 1662
[5 empty] | Lodging |  |  | 1460
[5 empty] | Multifamily |  |  | 1349
[5 empty] | Office - Large |  |  | 1084
[5 empty] | Office - Small |  |  | 882
[5 empty] | Restaurant |  |  | 1249
[5 empty] | Retail - Large |  |  | 845
[5 empty] | Retail - Small |  |  | 780
[5 empty] | Warehouse |  |  | 864
[5 empty] | Convenience |  |  | 1351
[5 empty] | Industrial |  |  | 1063
[5 empty] | Religious |  |  | 1031
[5 empty] | Nonresidential Average |  |  | 915
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 776
[5 empty] | Health |  |  | 1482
[5 empty] | Hospital |  |  | 1422
[5 empty] | Lodging |  |  | 1204
[5 empty] | Office - Large |  |  | 816
[5 empty] | Office - Small |  |  | 616
[5 empty] | Restaurant |  |  | 915
[5 empty] | Retail - Large |  |  | 764
[5 empty] | Retail - Small |  |  | 749
[5 empty] | Warehouse |  |  | 223
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 560
[5 empty] | Education |  | Zone 6 (Mason City) | 464
[5 empty] | Health |  |  | 1073
[5 empty] | Hospital |  |  | 946
[5 empty] | Lodging |  |  | 813
[5 empty] | Office - Large |  |  | 641
[5 empty] | Office - Small |  |  | 448
[5 empty] | Restaurant |  |  | 572
[5 empty] | Retail - Large |  |  | 504
[5 empty] | Retail - Small |  |  | 486
[5 empty] | Warehouse |  |  | 35
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 338
[5 empty] | Education |  | Average/Unknown | 645
[5 empty] | Health |  |  | 1328
[5 empty] | Hospital |  |  | 1356
[5 empty] | Lodging |  |  | 1105
[5 empty] | Office - Large |  |  | 823
[5 empty] | Office - Small |  |  | 542
[5 empty] | Restaurant |  |  | 825
[5 empty] | Retail - Large |  |  | 711
[5 empty] | Retail - Small |  |  | 744
[5 empty] | Warehouse |  |  | 148
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 488
| [ΔTAVG,cooling] | Climate Zone | Zone 5 (Burlington) |  |  |  |  | 20.4 | N | ⁰F | Average temperature difference [⁰F] during cooling season between outdoor air temperature and assumed 60⁰F duct supply air temperature
|  |  | Zone 6 (Mason City) |  |  |  |  | 15.2
|  |  | Average/Unknown |  |  |  |  | 18.6
| [1,000] | [7 empty] | N | Btu to kBtu | Conversion from Btu to kBtu
| [ηcooling] | [7 empty] | Y | kBtu/kWh | Seasonal energy efficiency ratio (SEER) of cooling system
| [EFLHHeat] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1298 | N | Hours | Equivalent Full Load Hours for heating space
[5 empty] | Grocery |  |  | 1493
[5 empty] | Health |  |  | 1206
[5 empty] | Hospital |  |  | 1084
[5 empty] | Lodging |  |  | 1365
[5 empty] | Multifamily |  |  | 1521
[5 empty] | Office - Large |  |  | 1457
[5 empty] | Office - Small |  |  | 1250
[5 empty] | Restaurant |  |  | 1040
[5 empty] | Retail - Large |  |  | 1255
[5 empty] | Retail - Small |  |  | 1172
[5 empty] | Warehouse |  |  | 1277
[5 empty] | Convenience |  |  | 785
[5 empty] | Industrial |  |  | 849
[5 empty] | Religious |  |  | 1322
[5 empty] | Nonresidential Average |  |  | 1251
[5 empty] | Education |  | Zone 6 (Mason City) | 1529
[5 empty] | Grocery |  |  | 1754
[5 empty] | Health |  |  | 1430
[5 empty] | Hospital |  |  | 940
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1846
[5 empty] | Office - Large |  |  | 1748
[5 empty] | Office - Small |  |  | 1435
[5 empty] | Restaurant |  |  | 1324
[5 empty] | Retail - Large |  |  | 1523
[5 empty] | Retail - Small |  |  | 1471
[5 empty] | Warehouse |  |  | 1589
[5 empty] | Convenience |  |  | 1224
[5 empty] | Industrial |  |  | 1275
[5 empty] | Religious |  |  | 1873
[5 empty] | Nonresidential Average |  |  | 1555
[5 empty] | Education |  | Average/Unknown | 1351
[5 empty] | Grocery |  |  | 1601
[5 empty] | Health |  |  | 1346
[5 empty] | Hospital |  |  | 1082
[5 empty] | Lodging |  |  | 1494
[5 empty] | Multifamily |  |  | 1694
[5 empty] | Office - Large |  |  | 1549
[5 empty] | Office - Small |  |  | 1358
[5 empty] | Restaurant |  |  | 1173
[5 empty] | Retail - Large |  |  | 1348
[5 empty] | Retail - Small |  |  | 1372
[5 empty] | Warehouse |  |  | 1443
[5 empty] | Convenience |  |  | 1071
[5 empty] | Industrial |  |  | 1183
[5 empty] | Religious |  |  | 1796
[5 empty] | Nonresidential Average |  |  | 1438
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 510
[5 empty] | Health |  |  | 778
[5 empty] | Hospital |  |  | 1799
[5 empty] | Lodging |  |  | 1080
[5 empty] | Office - Large |  |  | 710
[5 empty] | Office - Small |  |  | 450
[5 empty] | Restaurant |  |  | 896
[5 empty] | Retail - Large |  |  | 709
[5 empty] | Retail - Small |  |  | 785
[5 empty] | Warehouse |  |  | 886
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 690
[5 empty] | Education |  | Zone 6 (Mason City) | 683
[5 empty] | Health |  |  | 972
[5 empty] | Hospital |  |  | 1520
[5 empty] | Lodging |  |  | 1491
[5 empty] | Office - Large |  |  | 917
[5 empty] | Office - Small |  |  | 590
[5 empty] | Restaurant |  |  | 1192
[5 empty] | Retail - Large |  |  | 906
[5 empty] | Retail - Small |  |  | 1036
[5 empty] | Warehouse |  |  | 1238
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 930
[5 empty] | Education |  | Average/Unknown | 591
[5 empty] | Health |  |  | 864
[5 empty] | Hospital |  |  | 2196
[5 empty] | Lodging |  |  | 1471
[5 empty] | Office - Large |  |  | 862
[5 empty] | Office - Small |  |  | 492
[5 empty] | Restaurant |  |  | 1048
[5 empty] | Retail - Large |  |  | 839
[5 empty] | Retail - Small |  |  | 986
[5 empty] | Warehouse |  |  | 1116
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 830
| [ΔTAVG,heating] | Climate Zone | Zone 5 (Burlington) |  |  |  |  | 75.4 | N | ⁰F | Average temperature difference [⁰F] during heating season between outdoor air temperature and assumed 115⁰F duct supply air temperature
|  |  | Zone 6 (Mason City) |  |  |  |  | 84.9
|  |  | Average/Unknown |  |  |  |  | 79.1
| [3412] | [6 empty] | 3412 | N | Btu to kWh | Conversion from Btu to kBtu
| [ηheating] | [7 empty] | Y |  | Efficiency of heating system. Note: electric resistance heating and heat pumps will have an efficiency greater than or equal to 100%
| [∆Therms] | [7 empty] | C | Therms | Gas savings calculated with equation below
| [Fe] | [6 empty] | 3.14% | N |  | Percentage of heating energy consumed by fans
| [CF] | Building Type | Convenience |  |  |  |  | 92.3% | N |  | Summer Peak Coincidence Factor for Cooling
|  |  | Education |  |  |  |  | 96.7%
|  |  | Grocery |  |  |  |  | 100%
|  |  | Health |  |  |  |  | 100%
|  |  | Hospital |  |  |  |  | 98.6%
|  |  | Industrial |  |  |  |  | 44.6%
|  |  | Lodging |  |  |  |  | 97.4%
|  |  | Multifamily |  |  |  |  | 100%
|  |  | Office - Large |  |  |  |  | 98.8%
|  |  | Office - Small |  |  |  |  | 100%
|  |  | Religious |  |  |  |  | 94.3%
|  |  | Restaurant |  |  |  |  | 99.6%
|  |  | Retail - Large |  |  |  |  | 87.6%
|  |  | Retail - Small |  |  |  |  | 100%
|  |  | Warehouse |  |  |  |  | 77.9%
|  |  | Nonresidential Average |  |  |  |  | 92.3%
| [100000] | [7 empty] | N | Btus to Therms | Conversion from Btus to Therms
| [ηheat] | [7 empty] | Y |  | Efficiency of heating system
| [GCF] | Building Type | Convenience |  |  |  |  | 0.016482 | N |  | Gas Coincidence Factor for Heating
|  |  | Education |  |  |  |  | 0.01148
|  |  | Grocery |  |  |  |  | 0.013083
|  |  | Health |  |  |  |  | 0.010179
|  |  | Hospital |  |  |  |  | 0.015543
|  |  | Industrial |  |  |  |  | 0.014296
|  |  | Lodging |  |  |  |  | 0.013205
|  |  | Multifamily |  |  |  |  | 0.012268
|  |  | Office - Large |  |  |  |  | 0.013082
|  |  | Office - Small |  |  |  |  | 0.016718
|  |  | Religious |  |  |  |  | 0.011964
|  |  | Restaurant |  |  |  |  | 0.015262
|  |  | Retail - Large |  |  |  |  | 0.013281
|  |  | Retail - Small |  |  |  |  | 0.014055
|  |  | Warehouse |  |  |  |  | 0.015677
|  |  | Nonresidential Average |  |  |  |  | 0.014658

## Duct Repair Sealing Blower Door
Duct Repair Sealing Blower Door
| Measure Code: | NR-HVC-DCTS-V02-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [∆kWh_cooling] + [∆kWh_heating]
| Time of Sale Demand (ΔkW) | = [∆kWhcooling ] / [EFLHcooling] * [CF]
| Time of Sale Gas (ΔTherms) | = (([CFM_Pre] - [CFM_Post]) * [60] * [EFLH_heating] * [∆T_AVG,heating] * [0.018]) / (([η_heating] * [100,000]))
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [∆kWh_cooling] |  |  | = (([CFM_Pre] - [CFM_Post]) * [60] * [EFLH_cooling] * [∆T_AVG,cooling] * [0.018] * [LM]) / (([1000] * [η_cooling]))
| [∆kWh_heating] | Heating Type | Electric or Resistance | = (([CFM_Pre] - [CFM_Post])* [60] * [EFLH_heating] * [∆T_AVG,heating] * [0.018]) / (([η_heating] * [3,412]))
|  |  | Gas Furnace | = [Δtherms] * [Fe] * [29.3]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [∆kWh_cooling] | [7 empty] | C |  | If central cooling, reduction in annual cooling requirement due to air sealing
| [CFMPre] | [7 empty] | Y |  | Average duct leakage to exterior at normal operating conditions as estimated by professional testing before air sealing
| [CFMPost] | [7 empty] | Y |  | Average duct leakage to exterior at normal operating conditions as estimated by professional testing after air sealing
| [60] | [7 empty] | N |  | Converts Cubic Feet per Minute to Cubic Feet per Hour
| [EFLHCool] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1073 | N | Hours | Equivalent Full Load Hours for cooling
[5 empty] | Grocery |  |  | 320
[5 empty] | Health |  |  | 1449
[5 empty] | Hospital |  |  | 1792
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1472
[5 empty] | Office - Large |  |  | 1141
[5 empty] | Office - Small |  |  | 986
[5 empty] | Restaurant |  |  | 1397
[5 empty] | Retail - Large |  |  | 846
[5 empty] | Retail - Small |  |  | 891
[5 empty] | Warehouse |  |  | 1032
[5 empty] | Convenience |  |  | 1477
[5 empty] | Industrial |  |  | 1185
[5 empty] | Religious |  |  | 1109
[5 empty] | Nonresidential Average |  |  | 1034
[5 empty] | Education |  | Zone 6 (Mason City) | 848
[5 empty] | Grocery |  |  | 221
[5 empty] | Health |  |  | 996
[5 empty] | Hospital |  |  | 1436
[5 empty] | Lodging |  |  | 1252
[5 empty] | Multifamily |  |  | 1045
[5 empty] | Office - Large |  |  | 843
[5 empty] | Office - Small |  |  | 667
[5 empty] | Restaurant |  |  | 937
[5 empty] | Retail - Large |  |  | 616
[5 empty] | Retail - Small |  |  | 531
[5 empty] | Warehouse |  |  | 539
[5 empty] | Convenience |  |  | 1128
[5 empty] | Industrial |  |  | 856
[5 empty] | Religious |  |  | 797
[5 empty] | Nonresidential Average |  |  | 669
[5 empty] | Education |  | Average/Unknown | 928
[5 empty] | Grocery |  |  | 356
[5 empty] | Health |  |  | 1207
[5 empty] | Hospital |  |  | 1662
[5 empty] | Lodging |  |  | 1460
[5 empty] | Multifamily |  |  | 1349
[5 empty] | Office - Large |  |  | 1084
[5 empty] | Office - Small |  |  | 882
[5 empty] | Restaurant |  |  | 1249
[5 empty] | Retail - Large |  |  | 845
[5 empty] | Retail - Small |  |  | 780
[5 empty] | Warehouse |  |  | 864
[5 empty] | Convenience |  |  | 1351
[5 empty] | Industrial |  |  | 1063
[5 empty] | Religious |  |  | 1031
[5 empty] | Nonresidential Average |  |  | 915
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 776
[5 empty] | Health |  |  | 1482
[5 empty] | Hospital |  |  | 1422
[5 empty] | Lodging |  |  | 1204
[5 empty] | Office - Large |  |  | 816
[5 empty] | Office - Small |  |  | 616
[5 empty] | Restaurant |  |  | 915
[5 empty] | Retail - Large |  |  | 764
[5 empty] | Retail - Small |  |  | 749
[5 empty] | Warehouse |  |  | 223
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 560
[5 empty] | Education |  | Zone 6 (Mason City) | 464
[5 empty] | Health |  |  | 1073
[5 empty] | Hospital |  |  | 946
[5 empty] | Lodging |  |  | 813
[5 empty] | Office - Large |  |  | 641
[5 empty] | Office - Small |  |  | 448
[5 empty] | Restaurant |  |  | 572
[5 empty] | Retail - Large |  |  | 504
[5 empty] | Retail - Small |  |  | 486
[5 empty] | Warehouse |  |  | 35
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 338
[5 empty] | Education |  | Average/Unknown | 645
[5 empty] | Health |  |  | 1328
[5 empty] | Hospital |  |  | 1356
[5 empty] | Lodging |  |  | 1105
[5 empty] | Office - Large |  |  | 823
[5 empty] | Office - Small |  |  | 542
[5 empty] | Restaurant |  |  | 825
[5 empty] | Retail - Large |  |  | 711
[5 empty] | Retail - Small |  |  | 744
[5 empty] | Warehouse |  |  | 148
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 488
| [ΔTAVG,cooling] | Climate Zone | Zone 5 (Burlington) |  |  |  |  | 20.4 | N | ⁰F | Average temperature difference [⁰F] during cooling season between outdoor air temperature and assumed 60⁰F duct supply air temperature
|  |  | Zone 6 (Mason City) |  |  |  |  | 15.2
|  |  | Average/Unknown |  |  |  |  | 18.6
| [0.018] | [6 empty] | 0.018 | N | Btu/ft3*°F | Specific Heat Capacity of Air (Btu/ft3*°F)
| [LM] | Climate Zone | Zone 5 (Burlington) |  |  |  |  | 5 | N |  | Latent multiplier to account for latent cooling demand
|  |  | Zone 6 (Mason City) |  |  |  |  | 5.2
|  |  | Average/Unknown |  |  |  |  | 5.9
| [1000] | [6 empty] | 1000 | N | Btu to kBtu | Converts Btu to kBtu
| [ηcooling] | [7 empty] | Y | kBtu/kWh | Seasonal energy efficiency ratio (SEER) of cooling system (kBtu/kWh)
| [∆kWh_heating] | [7 empty] | C |  | If electric heat (resistance or heat pump), reduction in annual electric heating due to air sealing
| [EFLHHeat] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1298 | N | Hours | Equivalent Full Load Hours for heating space
[5 empty] | Grocery |  |  | 1493
[5 empty] | Health |  |  | 1206
[5 empty] | Hospital |  |  | 1084
[5 empty] | Lodging |  |  | 1365
[5 empty] | Multifamily |  |  | 1521
[5 empty] | Office - Large |  |  | 1457
[5 empty] | Office - Small |  |  | 1250
[5 empty] | Restaurant |  |  | 1040
[5 empty] | Retail - Large |  |  | 1255
[5 empty] | Retail - Small |  |  | 1172
[5 empty] | Warehouse |  |  | 1277
[5 empty] | Convenience |  |  | 785
[5 empty] | Industrial |  |  | 849
[5 empty] | Religious |  |  | 1322
[5 empty] | Nonresidential Average |  |  | 1251
[5 empty] | Education |  | Zone 6 (Mason City) | 1529
[5 empty] | Grocery |  |  | 1754
[5 empty] | Health |  |  | 1430
[5 empty] | Hospital |  |  | 940
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1846
[5 empty] | Office - Large |  |  | 1748
[5 empty] | Office - Small |  |  | 1435
[5 empty] | Restaurant |  |  | 1324
[5 empty] | Retail - Large |  |  | 1523
[5 empty] | Retail - Small |  |  | 1471
[5 empty] | Warehouse |  |  | 1589
[5 empty] | Convenience |  |  | 1224
[5 empty] | Industrial |  |  | 1275
[5 empty] | Religious |  |  | 1873
[5 empty] | Nonresidential Average |  |  | 1555
[5 empty] | Education |  | Average/Unknown | 1351
[5 empty] | Grocery |  |  | 1601
[5 empty] | Health |  |  | 1346
[5 empty] | Hospital |  |  | 1082
[5 empty] | Lodging |  |  | 1494
[5 empty] | Multifamily |  |  | 1694
[5 empty] | Office - Large |  |  | 1549
[5 empty] | Office - Small |  |  | 1358
[5 empty] | Restaurant |  |  | 1173
[5 empty] | Retail - Large |  |  | 1348
[5 empty] | Retail - Small |  |  | 1372
[5 empty] | Warehouse |  |  | 1443
[5 empty] | Convenience |  |  | 1071
[5 empty] | Industrial |  |  | 1183
[5 empty] | Religious |  |  | 1796
[5 empty] | Nonresidential Average |  |  | 1438
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 510
[5 empty] | Health |  |  | 778
[5 empty] | Hospital |  |  | 1799
[5 empty] | Lodging |  |  | 1080
[5 empty] | Office - Large |  |  | 710
[5 empty] | Office - Small |  |  | 450
[5 empty] | Restaurant |  |  | 896
[5 empty] | Retail - Large |  |  | 709
[5 empty] | Retail - Small |  |  | 785
[5 empty] | Warehouse |  |  | 886
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 690
[5 empty] | Education |  | Zone 6 (Mason City) | 683
[5 empty] | Health |  |  | 972
[5 empty] | Hospital |  |  | 1520
[5 empty] | Lodging |  |  | 1491
[5 empty] | Office - Large |  |  | 917
[5 empty] | Office - Small |  |  | 590
[5 empty] | Restaurant |  |  | 1192
[5 empty] | Retail - Large |  |  | 906
[5 empty] | Retail - Small |  |  | 1036
[5 empty] | Warehouse |  |  | 1238
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 930
[5 empty] | Education |  | Average/Unknown | 591
[5 empty] | Health |  |  | 864
[5 empty] | Hospital |  |  | 2196
[5 empty] | Lodging |  |  | 1471
[5 empty] | Office - Large |  |  | 862
[5 empty] | Office - Small |  |  | 492
[5 empty] | Restaurant |  |  | 1048
[5 empty] | Retail - Large |  |  | 839
[5 empty] | Retail - Small |  |  | 986
[5 empty] | Warehouse |  |  | 1116
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 830
| [ΔTAVG,heating] | Climate Zone | Zone 5 (Burlington) |  |  |  |  | 75.4 | N | ⁰F | Average temperature difference [⁰F] during heating season between outdoor air temperature and assumed 115⁰F duct supply air temperature
|  |  | Zone 6 (Mason City) |  |  |  |  | 84.9
|  |  | Average/Unknown |  |  |  |  | 79.1
| [3,142] | [6 empty] | 3412 | N | Btu to kWh | Conversion from Btu to kWh
| [ηheating] | [7 empty] | Y |  | Efficiency of heating system, Note: electric resistance heating and heat pumps will have an efficiency greater than or equal to 100%
| [Fe] | [6 empty] | 3.14% | N |  | Furnace Fan energy consumption as a percentage of annual fuel consumption
| [29.3] | [6 empty] | 29.3 | N | kWh per therm | kWh per therm
| [CF] | Building Type | Convenience |  |  |  |  | 92.3% | N |  | Summer Peak Coincidence Factor for Cooling
|  |  | Education |  |  |  |  | 96.7%
|  |  | Grocery |  |  |  |  | 100%
|  |  | Health |  |  |  |  | 100%
|  |  | Hospital |  |  |  |  | 98.6%
|  |  | Industrial |  |  |  |  | 44.6%
|  |  | Lodging |  |  |  |  | 97.4%
|  |  | Multifamily |  |  |  |  | 100%
|  |  | Office - Large |  |  |  |  | 98.8%
|  |  | Office - Small |  |  |  |  | 100%
|  |  | Religious |  |  |  |  | 94.3%
|  |  | Restaurant |  |  |  |  | 99.6%
|  |  | Retail - Large |  |  |  |  | 87.6%
|  |  | Retail - Small |  |  |  |  | 100%
|  |  | Warehouse |  |  |  |  | 77.9%
|  |  | Nonresidential Average |  |  |  |  | 92.3%
| [100,000] | [6 empty] | 100000 | N |  | Conversion from Btus to Therms
| [Δtherms] | [7 empty] | C | therms | Therm impact calcualted above
| [GCF] | Building Type | Convenience |  |  |  |  | 0.016482 | N |  | Gas Coincidence Factor for Heating
|  |  | Education |  |  |  |  | 0.01148
|  |  | Grocery |  |  |  |  | 0.013083
|  |  | Health |  |  |  |  | 0.010179
|  |  | Hospital |  |  |  |  | 0.015543
|  |  | Industrial |  |  |  |  | 0.014296
|  |  | Lodging |  |  |  |  | 0.013205
|  |  | Multifamily |  |  |  |  | 0.012268
|  |  | Office - Large |  |  |  |  | 0.013082
|  |  | Office - Small |  |  |  |  | 0.016718
|  |  | Religious |  |  |  |  | 0.011964
|  |  | Restaurant |  |  |  |  | 0.015262
|  |  | Retail - Large |  |  |  |  | 0.013281
|  |  | Retail - Small |  |  |  |  | 0.014055
|  |  | Warehouse |  |  |  |  | 0.015677
|  |  | Nonresidential Average |  |  |  |  | 0.014658

## Duct Repair Sealing Deemed
Duct Repair Sealing Deemed
| Measure Code: | NR-HVC-DCTS-V02-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [∆kWh_cooling] + [∆kWh_heating]
| Time of Sale Demand (ΔkW) | = [∆kWhcooling ] / [EFLHcooling] * [CF]
| Time of Sale Gas (ΔTherms) | = [SavingsPerUnitGas] * [L_Duct]
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [∆kWh_cooling] |  |  | = [SavingsPerUnitElec] * [L_Duct]
| [∆kWh_heating] | Heating Type | Electric or Resistance | = [SavingsPerUnitElec] * [L_Duct]
|  |  | Gas Furnace | = [Δtherms] * [Fe] * [29.3]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [SavingsPerUnitElec] | End Use | Cooling DX | HVAC System | Air Conditioning |  |  | 1.64 | N | kWh/ft | Annual savings per linear foot, dependent on heating / cooling equipment. Note: savings factors are additive. For example, a building with both heating and cooling provided by heat pumps would save (1.64+3.27) = 4.91 kWh/ft
|  |  | Space Heat |  | Electric Resistance /Furance |  |  | 5
|  |  | Heat Pump - Cooling |  | Heat Pump |  |  | 1.64
|  |  | Heat Pump - Heating |  | Heat Pump |  |  | 3.27
| [Lduct] | [7 empty] | Y |  | Linear footage of exterior ductwork sealed
| [∆kWh_cooling] | [7 empty] | C |  | If central cooling, reduction in annual cooling requirement due to air sealing
| [EFLHCool] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1073 | N | Hours | Equivalent Full Load Hours for cooling
[5 empty] | Grocery |  |  | 320
[5 empty] | Health |  |  | 1449
[5 empty] | Hospital |  |  | 1792
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1472
[5 empty] | Office - Large |  |  | 1141
[5 empty] | Office - Small |  |  | 986
[5 empty] | Restaurant |  |  | 1397
[5 empty] | Retail - Large |  |  | 846
[5 empty] | Retail - Small |  |  | 891
[5 empty] | Warehouse |  |  | 1032
[5 empty] | Convenience |  |  | 1477
[5 empty] | Industrial |  |  | 1185
[5 empty] | Religious |  |  | 1109
[5 empty] | Nonresidential Average |  |  | 1034
[5 empty] | Education |  | Zone 6 (Mason City) | 848
[5 empty] | Grocery |  |  | 221
[5 empty] | Health |  |  | 996
[5 empty] | Hospital |  |  | 1436
[5 empty] | Lodging |  |  | 1252
[5 empty] | Multifamily |  |  | 1045
[5 empty] | Office - Large |  |  | 843
[5 empty] | Office - Small |  |  | 667
[5 empty] | Restaurant |  |  | 937
[5 empty] | Retail - Large |  |  | 616
[5 empty] | Retail - Small |  |  | 531
[5 empty] | Warehouse |  |  | 539
[5 empty] | Convenience |  |  | 1128
[5 empty] | Industrial |  |  | 856
[5 empty] | Religious |  |  | 797
[5 empty] | Nonresidential Average |  |  | 669
[5 empty] | Education |  | Average/Unknown | 928
[5 empty] | Grocery |  |  | 356
[5 empty] | Health |  |  | 1207
[5 empty] | Hospital |  |  | 1662
[5 empty] | Lodging |  |  | 1460
[5 empty] | Multifamily |  |  | 1349
[5 empty] | Office - Large |  |  | 1084
[5 empty] | Office - Small |  |  | 882
[5 empty] | Restaurant |  |  | 1249
[5 empty] | Retail - Large |  |  | 845
[5 empty] | Retail - Small |  |  | 780
[5 empty] | Warehouse |  |  | 864
[5 empty] | Convenience |  |  | 1351
[5 empty] | Industrial |  |  | 1063
[5 empty] | Religious |  |  | 1031
[5 empty] | Nonresidential Average |  |  | 915
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 776
[5 empty] | Health |  |  | 1482
[5 empty] | Hospital |  |  | 1422
[5 empty] | Lodging |  |  | 1204
[5 empty] | Office - Large |  |  | 816
[5 empty] | Office - Small |  |  | 616
[5 empty] | Restaurant |  |  | 915
[5 empty] | Retail - Large |  |  | 764
[5 empty] | Retail - Small |  |  | 749
[5 empty] | Warehouse |  |  | 223
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 560
[5 empty] | Education |  | Zone 6 (Mason City) | 464
[5 empty] | Health |  |  | 1073
[5 empty] | Hospital |  |  | 946
[5 empty] | Lodging |  |  | 813
[5 empty] | Office - Large |  |  | 641
[5 empty] | Office - Small |  |  | 448
[5 empty] | Restaurant |  |  | 572
[5 empty] | Retail - Large |  |  | 504
[5 empty] | Retail - Small |  |  | 486
[5 empty] | Warehouse |  |  | 35
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 338
[5 empty] | Education |  | Average/Unknown | 645
[5 empty] | Health |  |  | 1328
[5 empty] | Hospital |  |  | 1356
[5 empty] | Lodging |  |  | 1105
[5 empty] | Office - Large |  |  | 823
[5 empty] | Office - Small |  |  | 542
[5 empty] | Restaurant |  |  | 825
[5 empty] | Retail - Large |  |  | 711
[5 empty] | Retail - Small |  |  | 744
[5 empty] | Warehouse |  |  | 148
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 488
| [CF] | Building Type | Convenience |  |  |  |  | 92.3% | N |  | Summer Peak Coincidence Factor for Cooling
|  |  | Education |  |  |  |  | 96.7%
|  |  | Grocery |  |  |  |  | 100%
|  |  | Health |  |  |  |  | 100%
|  |  | Hospital |  |  |  |  | 98.6%
|  |  | Industrial |  |  |  |  | 44.6%
|  |  | Lodging |  |  |  |  | 97.4%
|  |  | Multifamily |  |  |  |  | 100%
|  |  | Office - Large |  |  |  |  | 98.8%
|  |  | Office - Small |  |  |  |  | 100%
|  |  | Religious |  |  |  |  | 94.3%
|  |  | Restaurant |  |  |  |  | 99.6%
|  |  | Retail - Large |  |  |  |  | 87.6%
|  |  | Retail - Small |  |  |  |  | 100%
|  |  | Warehouse |  |  |  |  | 77.9%
|  |  | Nonresidential Average |  |  |  |  | 92.3%
| [SavingsPerUnitGas] | End Use | Space Heat Boiler | HVAC System | Gas Boiler |  |  | 0.26 | N | therms/ft | Annual savings per linear foot, dependent on heating / cooling equipment
|  |  | Space Heat Furnace |  | Gas Furnace |  |  | 0.26
| [Δtherms] | [7 empty] | C | therms | Therm impact calcualted above
| [Fe] | [6 empty] | 3.14% | N |  | Furnace Fan energy consumption as a percentage of annual fuel consumption
| [29.3] | [6 empty] | 29.3 | N | kWh per therm | kWh per therm
| [GCF] | Building Type | Convenience |  |  |  |  | 0.016482 | N |  | Gas Coincidence Factor for Heating
|  |  | Education |  |  |  |  | 0.01148
|  |  | Grocery |  |  |  |  | 0.013083
|  |  | Health |  |  |  |  | 0.010179
|  |  | Hospital |  |  |  |  | 0.015543
|  |  | Industrial |  |  |  |  | 0.014296
|  |  | Lodging |  |  |  |  | 0.013205
|  |  | Multifamily |  |  |  |  | 0.012268
|  |  | Office - Large |  |  |  |  | 0.013082
|  |  | Office - Small |  |  |  |  | 0.016718
|  |  | Religious |  |  |  |  | 0.011964
|  |  | Restaurant |  |  |  |  | 0.015262
|  |  | Retail - Large |  |  |  |  | 0.013281
|  |  | Retail - Small |  |  |  |  | 0.014055
|  |  | Warehouse |  |  |  |  | 0.015677
|  |  | Nonresidential Average |  |  |  |  | 0.014658

## Chiller Pipe Insulation
Chiller Pipe Insulation
| Measure Code: | NR-HVC-CPIN-V03-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Insulation Thickness | 1 inch |  |  | 13.97
|  | 2 inches |  |  | 21.2
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = (([L_SP] + [L_OC]) * [EFLH_cooling] * ([HG_Base] - [HG_Eff])) / (([1,000] * [η_cooling]))
| Time of Sale Demand (ΔkW) | = [ΔkWh_cooling] / [EFLH_cooling] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [LSP] | [7 empty] | Y | ft | Length of straight pipe to be insulated (linear foot)
| [LOC] | [7 empty] | Y | ft | Total equivalent length of the other components (valves and tees) of pipe to be insulated
| [EFLHCool] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1073 | N | Hours | Equivalent Full Load Hours for cooling
[5 empty] | Grocery |  |  | 320
[5 empty] | Health |  |  | 1449
[5 empty] | Hospital |  |  | 1792
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1472
[5 empty] | Office - Large |  |  | 1141
[5 empty] | Office - Small |  |  | 986
[5 empty] | Restaurant |  |  | 1397
[5 empty] | Retail - Large |  |  | 846
[5 empty] | Retail - Small |  |  | 891
[5 empty] | Warehouse |  |  | 1032
[5 empty] | Convenience |  |  | 1477
[5 empty] | Industrial |  |  | 1185
[5 empty] | Religious |  |  | 1109
[5 empty] | Nonresidential Average |  |  | 1034
[5 empty] | Education |  | Zone 6 (Mason City) | 848
[5 empty] | Grocery |  |  | 221
[5 empty] | Health |  |  | 996
[5 empty] | Hospital |  |  | 1436
[5 empty] | Lodging |  |  | 1252
[5 empty] | Multifamily |  |  | 1045
[5 empty] | Office - Large |  |  | 843
[5 empty] | Office - Small |  |  | 667
[5 empty] | Restaurant |  |  | 937
[5 empty] | Retail - Large |  |  | 616
[5 empty] | Retail - Small |  |  | 531
[5 empty] | Warehouse |  |  | 539
[5 empty] | Convenience |  |  | 1128
[5 empty] | Industrial |  |  | 856
[5 empty] | Religious |  |  | 797
[5 empty] | Nonresidential Average |  |  | 669
[5 empty] | Education |  | Average/Unknown | 928
[5 empty] | Grocery |  |  | 356
[5 empty] | Health |  |  | 1207
[5 empty] | Hospital |  |  | 1662
[5 empty] | Lodging |  |  | 1460
[5 empty] | Multifamily |  |  | 1349
[5 empty] | Office - Large |  |  | 1084
[5 empty] | Office - Small |  |  | 882
[5 empty] | Restaurant |  |  | 1249
[5 empty] | Retail - Large |  |  | 845
[5 empty] | Retail - Small |  |  | 780
[5 empty] | Warehouse |  |  | 864
[5 empty] | Convenience |  |  | 1351
[5 empty] | Industrial |  |  | 1063
[5 empty] | Religious |  |  | 1031
[5 empty] | Nonresidential Average |  |  | 915
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 776
[5 empty] | Health |  |  | 1482
[5 empty] | Hospital |  |  | 1422
[5 empty] | Lodging |  |  | 1204
[5 empty] | Office - Large |  |  | 816
[5 empty] | Office - Small |  |  | 616
[5 empty] | Restaurant |  |  | 915
[5 empty] | Retail - Large |  |  | 764
[5 empty] | Retail - Small |  |  | 749
[5 empty] | Warehouse |  |  | 223
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 560
[5 empty] | Education |  | Zone 6 (Mason City) | 464
[5 empty] | Health |  |  | 1073
[5 empty] | Hospital |  |  | 946
[5 empty] | Lodging |  |  | 813
[5 empty] | Office - Large |  |  | 641
[5 empty] | Office - Small |  |  | 448
[5 empty] | Restaurant |  |  | 572
[5 empty] | Retail - Large |  |  | 504
[5 empty] | Retail - Small |  |  | 486
[5 empty] | Warehouse |  |  | 35
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 338
[5 empty] | Education |  | Average/Unknown | 645
[5 empty] | Health |  |  | 1328
[5 empty] | Hospital |  |  | 1356
[5 empty] | Lodging |  |  | 1105
[5 empty] | Office - Large |  |  | 823
[5 empty] | Office - Small |  |  | 542
[5 empty] | Restaurant |  |  | 825
[5 empty] | Retail - Large |  |  | 711
[5 empty] | Retail - Small |  |  | 744
[5 empty] | Warehouse |  |  | 148
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 488
| [HGBase/Eff] | Insulation Thickness | Bare |  |  |  |  | 47.1 | N | BTU/hr/ft | Average heat gain factor [BTU/hr/ft] for the baseline and efficient cases, respectively.
|  |  | 0.5 |  |  |  |  | 14.413
|  |  | 1 |  |  |  |  | 9.063
|  |  | 1.5 |  |  |  |  | 6.973
|  |  | 2 |  |  |  |  | 5.798
|  |  | 2.5 |  |  |  |  | 5.038
|  |  | 3 |  |  |  |  | 4.45
|  |  | 3.5 |  |  |  |  | 4.068
|  |  | 4 |  |  |  |  | 3.768
|  |  | 4.5 |  |  |  |  | 3.475
|  |  | 5 |  |  |  |  | 3.288
|  |  | 5.5 |  |  |  |  | 3.13
|  |  | 6 |  |  |  |  | 2.99
|  |  | 6.5 |  |  |  |  | 2.875
|  |  | 7 |  |  |  |  | 2.77
|  |  | 7.5 |  |  |  |  | 2.68
|  |  | 8 |  |  |  |  | 2.6
|  |  | 8.5 |  |  |  |  | 2.523
|  |  | 9 |  |  |  |  | 2.455
|  |  | 9.5 |  |  |  |  | 2.398
|  |  | 10 |  |  |  |  | 2.34
| [1,000] | [6 empty] | 1000 | N | Btu to kBtu | Conversion from Btu to kBtu
| [ηcooling] | [7 empty] | Y | kBtu/kWh | Energy efficiency ratio (EER) of cooling system (kBtu/kWh)
| [CF] | Building Type | Convenience |  |  |  |  | 92.3% | N |  | Summer Peak Coincidence Factor for Cooling
|  |  | Education |  |  |  |  | 96.7%
|  |  | Grocery |  |  |  |  | 100%
|  |  | Health |  |  |  |  | 100%
|  |  | Hospital |  |  |  |  | 98.6%
|  |  | Industrial |  |  |  |  | 44.6%
|  |  | Lodging |  |  |  |  | 97.4%
|  |  | Multifamily |  |  |  |  | 100%
|  |  | Office - Large |  |  |  |  | 98.8%
|  |  | Office - Small |  |  |  |  | 100%
|  |  | Religious |  |  |  |  | 94.3%
|  |  | Restaurant |  |  |  |  | 99.6%
|  |  | Retail - Large |  |  |  |  | 87.6%
|  |  | Retail - Small |  |  |  |  | 100%
|  |  | Warehouse |  |  |  |  | 77.9%
|  |  | Nonresidential Average |  |  |  |  | 92.3%

## Hydronic Heat Pipe Insulation
Hydronic Heat Pipe Insulation
| Measure Code: | NR-HVC-HPIN-V03-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known | Known |  |  | Actual
|  | Unknown | Insulation Thickness | 1 inch | 13.97
|  |  |  | 2 inches | 21.2
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | = (([L_SP] +[ L_OC]) * [EFLH_heating] * ([Q_Base - Q_Eff] ) * [TRF]) / (([100,000] * [η_heat]))
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [LSP] | [7 empty] | Y |  | Length of straight pipe to be insulated (linear foot)
| [LOC] | [7 empty] | Y | ft | Total equivalent length of the other components (valves and tees) of pipe to be insulated
| [EFLHHeat] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1298 | N | Hours | Equivalent Full Load Hours for heating space
[5 empty] | Grocery |  |  | 1493
[5 empty] | Health |  |  | 1206
[5 empty] | Hospital |  |  | 1084
[5 empty] | Lodging |  |  | 1365
[5 empty] | Multifamily |  |  | 1521
[5 empty] | Office - Large |  |  | 1457
[5 empty] | Office - Small |  |  | 1250
[5 empty] | Restaurant |  |  | 1040
[5 empty] | Retail - Large |  |  | 1255
[5 empty] | Retail - Small |  |  | 1172
[5 empty] | Warehouse |  |  | 1277
[5 empty] | Convenience |  |  | 785
[5 empty] | Industrial |  |  | 849
[5 empty] | Religious |  |  | 1322
[5 empty] | Nonresidential Average |  |  | 1251
[5 empty] | Education |  | Zone 6 (Mason City) | 1529
[5 empty] | Grocery |  |  | 1754
[5 empty] | Health |  |  | 1430
[5 empty] | Hospital |  |  | 940
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1846
[5 empty] | Office - Large |  |  | 1748
[5 empty] | Office - Small |  |  | 1435
[5 empty] | Restaurant |  |  | 1324
[5 empty] | Retail - Large |  |  | 1523
[5 empty] | Retail - Small |  |  | 1471
[5 empty] | Warehouse |  |  | 1589
[5 empty] | Convenience |  |  | 1224
[5 empty] | Industrial |  |  | 1275
[5 empty] | Religious |  |  | 1873
[5 empty] | Nonresidential Average |  |  | 1555
[5 empty] | Education |  | Average/Unknown | 1351
[5 empty] | Grocery |  |  | 1601
[5 empty] | Health |  |  | 1346
[5 empty] | Hospital |  |  | 1082
[5 empty] | Lodging |  |  | 1494
[5 empty] | Multifamily |  |  | 1694
[5 empty] | Office - Large |  |  | 1549
[5 empty] | Office - Small |  |  | 1358
[5 empty] | Restaurant |  |  | 1173
[5 empty] | Retail - Large |  |  | 1348
[5 empty] | Retail - Small |  |  | 1372
[5 empty] | Warehouse |  |  | 1443
[5 empty] | Convenience |  |  | 1071
[5 empty] | Industrial |  |  | 1183
[5 empty] | Religious |  |  | 1796
[5 empty] | Nonresidential Average |  |  | 1438
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 510
[5 empty] | Health |  |  | 778
[5 empty] | Hospital |  |  | 1799
[5 empty] | Lodging |  |  | 1080
[5 empty] | Office - Large |  |  | 710
[5 empty] | Office - Small |  |  | 450
[5 empty] | Restaurant |  |  | 896
[5 empty] | Retail - Large |  |  | 709
[5 empty] | Retail - Small |  |  | 785
[5 empty] | Warehouse |  |  | 886
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 690
[5 empty] | Education |  | Zone 6 (Mason City) | 683
[5 empty] | Health |  |  | 972
[5 empty] | Hospital |  |  | 1520
[5 empty] | Lodging |  |  | 1491
[5 empty] | Office - Large |  |  | 917
[5 empty] | Office - Small |  |  | 590
[5 empty] | Restaurant |  |  | 1192
[5 empty] | Retail - Large |  |  | 906
[5 empty] | Retail - Small |  |  | 1036
[5 empty] | Warehouse |  |  | 1238
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 930
[5 empty] | Education |  | Average/Unknown | 591
[5 empty] | Health |  |  | 864
[5 empty] | Hospital |  |  | 2196
[5 empty] | Lodging |  |  | 1471
[5 empty] | Office - Large |  |  | 862
[5 empty] | Office - Small |  |  | 492
[5 empty] | Restaurant |  |  | 1048
[5 empty] | Retail - Large |  |  | 839
[5 empty] | Retail - Small |  |  | 986
[5 empty] | Warehouse |  |  | 1116
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 830
| [QBase - Qeff] | Pipe Location | Indoor | System Type | Hot Water Space Heating - Without Outdoor Reset |  |  | 90 | N | BTU/hr/ft | Difference in heat loss rate due to the added insulation [BTU/hr/ft]
[5 empty] | Hot water Space Heating - With Outdoor Reset, Heating Season Only |  |  | 61
[5 empty] | Hot Water Space Heating - With Outdoor Reset, Year-Round |  |  | 45
[5 empty] | Low Pressure Stream |  |  | 192
[5 empty] | High Pressure Stream |  |  | 362
|  |  | Outdoor |  | Hot Water Space Heating - Without Outdoor Reset |  |  | 439
[5 empty] | Hot water Space Heating - With Outdoor Reset, Heating Season Only |  |  | 347
[5 empty] | Hot Water Space Heating - With Outdoor Reset, Year-Round |  |  | 293
[5 empty] | Low Pressure Stream |  |  | 678
[5 empty] | High Pressure Stream |  |  | 1049
| [1,000] | [6 empty] | 1000 | N |  | Conversion from Btu to kBtu
| [ηheat] | Boiler Type | Hot Water |  |  |  |  | 82% | Y |  | Efficiency of heating system
|  |  | Steam |  |  |  |  | 80%
| [TRF] | Pipe Location | Outdoor |  |  |  |  | 1 | N | Δtherms/ft | Thermal Regain Factor for space type, applied only to space heating energy and is applied to values resulting from Δtherms/ft
|  |  | Indoor, heated space |  |  |  |  | 0.15
|  |  | Indoor, semi- heated, (unconditioned space, with heat transfer to conditioned space. E.g.: boiler room, ceiling plenum, basement, crawlspace, wall) |  |  |  |  | 0.7
|  |  | Indoor, unheated, (not heat transfer to conditioned space) |  |  |  |  | 1
|  |  | Location not specified |  |  |  |  | 0.15
|  |  | Custom |  |  |  |  | 1 - assumed regain
| [Δtherms] | [7 empty] | C | Therms | Therm impact calcualted above
| [GCF] | Building Type | Convenience |  |  |  |  | 0.016482 | N |  | Gas Coincidence Factor for Heating
|  |  | Education |  |  |  |  | 0.01148
|  |  | Grocery |  |  |  |  | 0.013083
|  |  | Health |  |  |  |  | 0.010179
|  |  | Hospital |  |  |  |  | 0.015543
|  |  | Industrial |  |  |  |  | 0.014296
|  |  | Lodging |  |  |  |  | 0.013205
|  |  | Multifamily |  |  |  |  | 0.012268
|  |  | Office - Large |  |  |  |  | 0.013082
|  |  | Office - Small |  |  |  |  | 0.016718
|  |  | Religious |  |  |  |  | 0.011964
|  |  | Restaurant |  |  |  |  | 0.015262
|  |  | Retail - Large |  |  |  |  | 0.013281
|  |  | Retail - Small |  |  |  |  | 0.014055
|  |  | Warehouse |  |  |  |  | 0.015677
|  |  | Nonresidential Average |  |  |  |  | 0.014658

## Shut Off Damper...
Shut Off Damper for Psace Heating Boilers or Furnaces
| Measure Code: | NR-HVC-SODP-V02-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known | Known | Actual
|  | Unknown | 1500
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
|  |  | 1 | 150
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | =[N_gi] * [SF] * [EFLH ] / [100]
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Ngi] | [7 empty] | Y | kBtu/hr | Boiler gas input size
| [SF] | [6 empty] | 1% | N |  | Savings Factor, Note: The savings factor assumes the boiler or furnace is located in an unconditioned space. The savings factor can be higher for those units located within conditioned space.
| [EFLHHeat] | Construction Type | Existing Building | Building Type | Education | Climate Zone | Zone 5 (Burlington) | 1298 | N | Hours | Equivalent Full Load Hours for heating space
[5 empty] | Grocery |  |  | 1493
[5 empty] | Health |  |  | 1206
[5 empty] | Hospital |  |  | 1084
[5 empty] | Lodging |  |  | 1365
[5 empty] | Multifamily |  |  | 1521
[5 empty] | Office - Large |  |  | 1457
[5 empty] | Office - Small |  |  | 1250
[5 empty] | Restaurant |  |  | 1040
[5 empty] | Retail - Large |  |  | 1255
[5 empty] | Retail - Small |  |  | 1172
[5 empty] | Warehouse |  |  | 1277
[5 empty] | Convenience |  |  | 785
[5 empty] | Industrial |  |  | 849
[5 empty] | Religious |  |  | 1322
[5 empty] | Nonresidential Average |  |  | 1251
[5 empty] | Education |  | Zone 6 (Mason City) | 1529
[5 empty] | Grocery |  |  | 1754
[5 empty] | Health |  |  | 1430
[5 empty] | Hospital |  |  | 940
[5 empty] | Lodging |  |  | 1464
[5 empty] | Multifamily |  |  | 1846
[5 empty] | Office - Large |  |  | 1748
[5 empty] | Office - Small |  |  | 1435
[5 empty] | Restaurant |  |  | 1324
[5 empty] | Retail - Large |  |  | 1523
[5 empty] | Retail - Small |  |  | 1471
[5 empty] | Warehouse |  |  | 1589
[5 empty] | Convenience |  |  | 1224
[5 empty] | Industrial |  |  | 1275
[5 empty] | Religious |  |  | 1873
[5 empty] | Nonresidential Average |  |  | 1555
[5 empty] | Education |  | Average/Unknown | 1351
[5 empty] | Grocery |  |  | 1601
[5 empty] | Health |  |  | 1346
[5 empty] | Hospital |  |  | 1082
[5 empty] | Lodging |  |  | 1494
[5 empty] | Multifamily |  |  | 1694
[5 empty] | Office - Large |  |  | 1549
[5 empty] | Office - Small |  |  | 1358
[5 empty] | Restaurant |  |  | 1173
[5 empty] | Retail - Large |  |  | 1348
[5 empty] | Retail - Small |  |  | 1372
[5 empty] | Warehouse |  |  | 1443
[5 empty] | Convenience |  |  | 1071
[5 empty] | Industrial |  |  | 1183
[5 empty] | Religious |  |  | 1796
[5 empty] | Nonresidential Average |  |  | 1438
|  |  | New Construction |  | Education |  | Zone 5 (Burlington) | 510
[5 empty] | Health |  |  | 778
[5 empty] | Hospital |  |  | 1799
[5 empty] | Lodging |  |  | 1080
[5 empty] | Office - Large |  |  | 710
[5 empty] | Office - Small |  |  | 450
[5 empty] | Restaurant |  |  | 896
[5 empty] | Retail - Large |  |  | 709
[5 empty] | Retail - Small |  |  | 785
[5 empty] | Warehouse |  |  | 886
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 690
[5 empty] | Education |  | Zone 6 (Mason City) | 683
[5 empty] | Health |  |  | 972
[5 empty] | Hospital |  |  | 1520
[5 empty] | Lodging |  |  | 1491
[5 empty] | Office - Large |  |  | 917
[5 empty] | Office - Small |  |  | 590
[5 empty] | Restaurant |  |  | 1192
[5 empty] | Retail - Large |  |  | 906
[5 empty] | Retail - Small |  |  | 1036
[5 empty] | Warehouse |  |  | 1238
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 930
[5 empty] | Education |  | Average/Unknown | 591
[5 empty] | Health |  |  | 864
[5 empty] | Hospital |  |  | 2196
[5 empty] | Lodging |  |  | 1471
[5 empty] | Office - Large |  |  | 862
[5 empty] | Office - Small |  |  | 492
[5 empty] | Restaurant |  |  | 1048
[5 empty] | Retail - Large |  |  | 839
[5 empty] | Retail - Small |  |  | 986
[5 empty] | Warehouse |  |  | 1116
[5 empty] | Convenience |  |  | n/a
[5 empty] | Industrial |  |  | n/a
[5 empty] | Religious |  |  | n/a
[5 empty] | Grocery |  |  | n/a
[5 empty] | Multifamily |  |  | n/a
[5 empty] | Nonresidential Average |  |  | 830
| [100] | [6 empty] | 100 | N | kBtu to therms | Converts kBtu to therms
| [Δtherms] | [7 empty] | C | Therms | Therm impact calcualted above
| [GCF] | Building Type | Convenience |  |  |  |  | 0.016482 | N |  | Gas Coincidence Factor for Heating
|  |  | Education |  |  |  |  | 0.01148
|  |  | Grocery |  |  |  |  | 0.013083
|  |  | Health |  |  |  |  | 0.010179
|  |  | Hospital |  |  |  |  | 0.015543
|  |  | Industrial |  |  |  |  | 0.014296
|  |  | Lodging |  |  |  |  | 0.013205
|  |  | Multifamily |  |  |  |  | 0.012268
|  |  | Office - Large |  |  |  |  | 0.013082
|  |  | Office - Small |  |  |  |  | 0.016718
|  |  | Religious |  |  |  |  | 0.011964
|  |  | Restaurant |  |  |  |  | 0.015262
|  |  | Retail - Large |  |  |  |  | 0.013281
|  |  | Retail - Small |  |  |  |  | 0.014055
|  |  | Warehouse |  |  |  |  | 0.015677
|  |  | Nonresidential Average |  |  |  |  | 0.014658

## Room AC
Room AC
| Measure Code: | NR-HVC-RMAC-V02-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
9
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| ENERGY STAR unit |  | 50
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = (([FLHRoomAC] * [Btu/H] * (1 / [CEERbase] - 1 / [CEERee])) / [1000]
| Time of Sale Demand (ΔkW) | = ([Btu/H] * (1 / ([CEERbase] * [1.01]) - 1 / ([CEERee] * [1.01]))) / [1000] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [FLHRoomAC] | Building Type | Convenience | Climate Zone | Zone 5 (Burlington) | 458 | N | Hours | Full Load Hours of room air conditioning unit
|  |  | Education |  |  | 328
|  |  | Grocery |  |  | 612
|  |  | Health |  |  | 362
|  |  | Hospital |  |  | 571
|  |  | Industrial |  |  | 367
|  |  | Lodging |  |  | 466
|  |  | Multifamily |  |  | 466
|  |  | Office - Large |  |  | 380
|  |  | Office - Small |  |  | 339
|  |  | Religious |  |  | 344
|  |  | Restaurant |  |  | 411
|  |  | Retail - Large |  |  | 375
|  |  | Retail - Small |  |  | 365
|  |  | Warehouse |  |  | 296
|  |  | Nonresidential Average |  |  | 337
|  |  | Convenience |  | Zone 6 (Mason City) | 350
|  |  | Education |  |  | 221
|  |  | Grocery |  |  | 460
|  |  | Health |  |  | 278
|  |  | Hospital |  |  | 423
|  |  | Industrial |  |  | 265
|  |  | Lodging |  |  | 336
|  |  | Multifamily |  |  | 336
|  |  | Office - Large |  |  | 301
|  |  | Office - Small |  |  | 244
|  |  | Religious |  |  | 247
|  |  | Restaurant |  |  | 296
|  |  | Retail - Large |  |  | 267
|  |  | Retail - Small |  |  | 261
|  |  | Warehouse |  |  | 215
|  |  | Nonresidential Average |  |  | 241
|  |  | Convenience |  | Average/Unknown | 419
|  |  | Education |  |  | 290
|  |  | Grocery |  |  | 538
|  |  | Health |  |  | 330
|  |  | Hospital |  |  | 519
|  |  | Industrial |  |  | 330
|  |  | Lodging |  |  | 420
|  |  | Multifamily |  |  | 420
|  |  | Office - Large |  |  | 354
|  |  | Office - Small |  |  | 304
|  |  | Religious |  |  | 320
|  |  | Restaurant |  |  | 365
|  |  | Retail - Large |  |  | 334
|  |  | Retail - Small |  |  | 322
|  |  | Warehouse |  |  | 268
|  |  | Nonresidential Average |  |  | 303
| [Btu/Hr] |  |  |  |  | 8500 | Y | Btu/hr | Size of unit
| [CEERbase] | Product Class (Btu/H) | < 8,000 | Federal Standard CEERbase, with louvered sides, without reverse cycle |  | 11 | N |  | Efficiency of baseline unit
|  |  | 8,000 to 10,999 |  |  | 10.9
|  |  | 11,000 to 13,999 |  |  | 10.9
|  |  | 14,000 to 19,999 |  |  | 10.7
|  |  | 20,000 to 24,999 |  |  | 9.4
|  |  | 25,000-27,999 |  |  | 9
|  |  | >=28,000 |  |  | 9
|  |  | < 8,000 | Federal Standard CEERbase, without louvered sides, without reverse cycle |  | 10
|  |  | 8,000 to 10,999 |  |  | 9.6
|  |  | 11,000 to 13,999 |  |  | 9.5
|  |  | 14,000 to 19,999 |  |  | 9.3
|  |  | 20,000 to 24,999 |  |  | 9.4
|  |  | 25,000-27,999 |  |  | 9.4
|  |  | >=28,000 |  |  | 9.4
|  | Casement | Casement-only | Federal Standard CEERbase |  | 9.5
|  |  | Casement-slider |  |  | 10.4
|  | Reverse Cycle - Product Class (Btu/H) | < 14,000 | Federal Standard CEERbase, with louvered sides |  | N/A
|  |  | >= 14,000 |  |  | N/A
|  |  | < 20,000 |  |  | 9.8
|  |  | >= 20,000 |  |  | 9.3
|  |  | < 14,000 | Federal Standard CEERbase, without louvered sides |  | 9.3
|  |  | >= 14,000 |  |  | 8.7
|  |  | < 20,000 |  |  | N/A
|  |  | >= 20,000 |  |  | N/A
| [CEERee] | Product Class (Btu/H) | < 8,000 | ENERGY STAR CEERee, with louvered sides |  | 12.1 | Y |  | Efficiency of ENERGY STAR unit
|  |  | 8,000 to 10,999 |  |  | 12
|  |  | 11,000 to 13,999 |  |  | 12
|  |  | 14,000 to 19,999 |  |  | 11.8
|  |  | 20,000 to 24,999 |  |  | 10.3
|  |  | 25,000-27,999 |  |  | 10.3
|  |  | >=28,000 |  |  | 9.9
|  |  | < 8,000 | ENERGY STAR CEERee, without louvered sides |  | 11
|  |  | 8,000 to 10,999 |  |  | 10.6
|  |  | 11,000 to 13,999 |  |  | 10.5
|  |  | 14,000 to 19,999 |  |  | 10.2
|  |  | 20,000 to 24,999 |  |  | 10.3
|  |  | 25,000-27,999 |  |  | 10.3
|  |  | >=28,000 |  |  | 10.3
|  | Casement | Casement-only | ENERGY STAR CEERee |  | 10.5
|  |  | Casement-slider |  |  | 11.4
|  | Reverse Cycle - Product Class (Btu/H) | < 14,000 | ENERGY STAR CEERee, with louvered sides |  | N/A
|  |  | >= 14,000 |  |  | N/A
|  |  | < 20,000 |  |  | 10.8
|  |  | >= 20,000 |  |  | 10.2
|  |  | < 14,000 | ENERGY STAR CEERee, without louvered sides |  | 10.2
|  |  | >= 14,000 |  |  | 9.6
|  |  | < 20,000 |  |  | N/A
|  |  | >= 20,000 |  |  | N/A
| [CF] |  |  |  |  | 0.3 | N |  | Summer Peak Coincidence Factor for measure
| [1.01] |  |  |  |  | 1.01 | N |  | Factor to convert CEER to EER (CEER includes standby and power off consumption)

## Room AC Recycling
Room AC Recycling
| Measure Code: | NR-APL-RACR-V02-180101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
3
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = ([Hours] * [BtuH]) / ([EERexist] / [1.01] * [1000]) - ([%replaced] * ([Hours] * [BtuH] ) / ([CEERNewBase] * [1000]))
| Time of Sale Demand (ΔkW) | = [ΔkWh] / [Hours] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [FLHRoomAC] | Building Type | Convenience | Climate Zone | Zone 5 (Burlington) | 458 | N | Hours | Full Load Hours of room air conditioning unit
|  |  | Education |  |  | 328
|  |  | Grocery |  |  | 612
|  |  | Health |  |  | 362
|  |  | Hospital |  |  | 571
|  |  | Industrial |  |  | 367
|  |  | Lodging |  |  | 466
|  |  | Multifamily |  |  | 466
|  |  | Office - Large |  |  | 380
|  |  | Office - Small |  |  | 339
|  |  | Religious |  |  | 344
|  |  | Restaurant |  |  | 411
|  |  | Retail - Large |  |  | 375
|  |  | Retail - Small |  |  | 365
|  |  | Warehouse |  |  | 296
|  |  | Nonresidential Average |  |  | 337
|  |  | Convenience |  | Zone 6 (Mason City) | 350
|  |  | Education |  |  | 221
|  |  | Grocery |  |  | 460
|  |  | Health |  |  | 278
|  |  | Hospital |  |  | 423
|  |  | Industrial |  |  | 265
|  |  | Lodging |  |  | 336
|  |  | Multifamily |  |  | 336
|  |  | Office - Large |  |  | 301
|  |  | Office - Small |  |  | 244
|  |  | Religious |  |  | 247
|  |  | Restaurant |  |  | 296
|  |  | Retail - Large |  |  | 267
|  |  | Retail - Small |  |  | 261
|  |  | Warehouse |  |  | 215
|  |  | Nonresidential Average |  |  | 241
|  |  | Convenience |  | Average/Unknown | 419
|  |  | Education |  |  | 290
|  |  | Grocery |  |  | 538
|  |  | Health |  |  | 330
|  |  | Hospital |  |  | 519
|  |  | Industrial |  |  | 330
|  |  | Lodging |  |  | 420
|  |  | Multifamily |  |  | 420
|  |  | Office - Large |  |  | 354
|  |  | Office - Small |  |  | 304
|  |  | Religious |  |  | 320
|  |  | Restaurant |  |  | 365
|  |  | Retail - Large |  |  | 334
|  |  | Retail - Small |  |  | 322
|  |  | Warehouse |  |  | 268
|  |  | Nonresidential Average |  |  | 303
| [BtuH] |  |  |  |  | 8500 | Y |  | Average size of rebated unit
| [EERexist] |  |  |  |  | 9.8 | Y |  | Efficiency of recycled unit
| [%replaced] | Scenario | Customer states unit will not be replaced |  |  | 0% | N |  | Percentage of units dropped off that are replaced
|  |  | Customer states unit will be replaced |  |  | 100%
|  |  | Unknown |  |  | 76%
| [CEERNewbase] |  |  |  |  | 10.9 | N |  | Efficiency of baseline unit
| [1.01] |  |  |  |  | 1.01 | N |  | Factor to convert EER to CEER (CEER includes standby and off power consumption
| [CF] |  |  |  |  | 0.3 | N |  | Summer Peak Coincidence Factor for measure

## Steam Trap Replacement
Steam Trap Replacement or Repair
| Measure Code: | NR-HVC-STRE-V02-200101
| Lifetime of Efficient Equipment: | [6 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
6
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Building Type | Commercial |  |  | 177
|  | Industrial | Maximum steam system operating pressure | ≤ 15 psig | 280
|  |  |  | > 15 ≤ 30 psig | 300
|  |  |  | > 30 ≤ 125 psig | 323
|  |  |  | > 125 ≤ 200 psig | 415
|  |  |  | > 200 ≤ 250 psig | 275
|  |  |  | > 250 psig | Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | = [LeakRate] * [H_vap] * [Hours_Heat] * [%Leak]/[EFF_Heat]/[100,000]
| Time of Sale Peak Gas (ΔPeakTherms) | = [∆Therms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [LeakRate] |  |  | = [24.24]* ([P_Inlet] + [14.7]) * [D²] * [%Adjust]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [LeakRate] | [7 empty] | C | lb/hr | Average steam loss rate per leaking trap
| [24.24] | [6 empty] | 24.24 | N | lb/(hr-psia-in2 | Constant from Napier's equation
| [P_inlet] | [7 empty] | Y | psig | Steam trap inlet pressure
| [14.7] | [6 empty] | 14.7 | N | psia | Atmospheric pressure
| [D] | [7 empty] | Y | in | Diameter of steam trap orifice
| [%Adjust] | [6 empty] | 50% | N |  | Adjustment factor to reduce the maximum theoretical steam flow to the average steam flow
| [H_vap] | P_inlet | 2 |  |  |  |  | 966 | N | Btu/lb | Heat of vaporization of steam
|  |  | 5 |  |  |  |  | 960
|  |  | 10 |  |  |  |  | 952
|  |  | 15 |  |  |  |  | 945
|  |  | 20 |  |  |  |  | 939
|  |  | 25 |  |  |  |  | 934
|  |  | 30 |  |  |  |  | 929
|  |  | 40 |  |  |  |  | 926
|  |  | 50 |  |  |  |  | 912
|  |  | 60 |  |  |  |  | 905
|  |  | 70 |  |  |  |  | 898
|  |  | 80 |  |  |  |  | 892
|  |  | 90 |  |  |  |  | 886
|  |  | 100 |  |  |  |  | 880
|  |  | 110 |  |  |  |  | 875
|  |  | 120 |  |  |  |  | 871
|  |  | 125 |  |  |  |  | 868
|  |  | 130 |  |  |  |  | 866
|  |  | 140 |  |  |  |  | 862
|  |  | 150 |  |  |  |  | 857
|  |  | 160 |  |  |  |  | 853
|  |  | 180 |  |  |  |  | 845
|  |  | 200 |  |  |  |  | 834
|  |  | 225 |  |  |  |  | 829
|  |  | 250 |  |  |  |  | 820
| [Hours_Heat} | [7 empty] | Y | Hours | Annual operating hours of steam plant
| [%Leak] | Number of traps replaced | One |  |  |  |  | 100% | N |  | Percentage of leaking or blow-through steam traps
|  |  | Multiple | System audited or not | Audited |  |  | 100%
[5 empty] | Not audited | Customer Type | Commercial | 27%
[7 empty] | Industrial | 16%
| [EFF_Heat] | [7 empty] | Y |  | Boiler efficiency
| [100,000] | [6 empty] | 100000 | N |  | Factor to convert Btus to therms
| [∆Therms] | [7 empty] | C | Therms | Therm impact calculated above
| [GCF] | Building Type | Convenience |  |  |  |  | 0.01631 | N |  | Gas coincidence factor for heating
|  |  | Education |  |  |  |  | 0.01148
|  |  | Grocery |  |  |  |  | 0.013083
|  |  | Health |  |  |  |  | 0.010179
|  |  | Hospital |  |  |  |  | 0.015543
|  |  | Industrial |  |  |  |  | 0.01424
|  |  | Lodging |  |  |  |  | 0.013205
|  |  | Multifamily |  |  |  |  | 0.012268
|  |  | Office - Large |  |  |  |  | 0.013082
|  |  | Office - Small |  |  |  |  | 0.016718
|  |  | Religious |  |  |  |  | 0.011745
|  |  | Restaurant |  |  |  |  | 0.015262
|  |  | Retail - Large |  |  |  |  | 0.013281
|  |  | Retail - Small |  |  |  |  | 0.014055
|  |  | Warehouse |  |  |  |  | 0.015677
|  |  | Nonresidential Average |  |  |  |  | 0.014623

## Electric HVAC Tune Up Custom
Electric HVAC Tune Up Custom
| Measure Code: | NR-HVC-ACTU-V01-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
3
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | ΔkWH= ([Capacity_Cool] * [(1/[EER_before]) – (1/[EER_after])] * [EFLH])/[1000]
| Time of Sale Demand (ΔkW) | ΔkW = [ΔkWh] / [EFLH] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [CapacityCool] | [5 empty] | Y | Btuh | Cooling Capacity of new equipment in Btu/hr (note 1 ton = 12,000Btu/hr)
| [EER_before] | [5 empty] | Y | EER | Energy Efficiency Ratio of unit before tune-up
| [EFFee] | [5 empty] | Y | EER | Energy Efficiency Ratio of unit after tune-up
| [EFLH] | Building Type | Education | Location | Zone 5 (Burlington) | 1073 | N | HOURS | Equivalent Full Load Hours for cooling in Existing Buildings
|  |  | Grocery |  |  | 320 | N | HOURS
|  |  | Health |  |  | 1449 | N | HOURS
|  |  | Hospital |  |  | 1792 | N | HOURS
|  |  | Lodging |  |  | 1464 | N | HOURS
|  |  | Multifamily |  |  | 1472 | N | HOURS
|  |  | Office - Large |  |  | 1141 | N | HOURS
|  |  | Office - Small |  |  | 986 | N | HOURS
|  |  | Restaurant |  |  | 1397 | N | HOURS
|  |  | Retail - Large |  |  | 846 | N | HOURS
|  |  | Retail - Small |  |  | 891 | N | HOURS
|  |  | Warehouse |  |  | 1032 | N | HOURS
|  |  | Convenience |  |  | 1477 | N | HOURS
|  |  | Industrial |  |  | 1185 | N | HOURS
|  |  | Religious |  |  | 1109 | N | HOURS
|  |  | Nonresidential Average |  |  | 1034 | N | HOURS
|  |  | Education |  | Zone 6 (Mason City) | 848 | N | HOURS
|  |  | Grocery |  |  | 221 | N | HOURS
|  |  | Health |  |  | 996 | N | HOURS
|  |  | Hospital |  |  | 1436 | N | HOURS
|  |  | Lodging |  |  | 1252 | N | HOURS
|  |  | Multifamily |  |  | 1045 | N | HOURS
|  |  | Office - Large |  |  | 843 | N | HOURS
|  |  | Office - Small |  |  | 667 | N | HOURS
|  |  | Restaurant |  |  | 937 | N | HOURS
|  |  | Retail - Large |  |  | 616 | N | HOURS
|  |  | Retail - Small |  |  | 531 | N | HOURS
|  |  | Warehouse |  |  | 539 | N | HOURS
|  |  | Convenience |  |  | 1128 | N | HOURS
|  |  | Industrial |  |  | 856 | N | HOURS
|  |  | Religious |  |  | 797 | N | HOURS
|  |  | Nonresidential Average |  |  | 669 | N | HOURS
|  |  | Education |  | Average/Unknown | 928 | N | HOURS
|  |  | Grocery |  |  | 356 | N | HOURS
|  |  | Health |  |  | 1207 | N | HOURS
|  |  | Hospital |  |  | 1662 | N | HOURS
|  |  | Lodging |  |  | 1460 | N | HOURS
|  |  | Multifamily |  |  | 1349 | N | HOURS
|  |  | Office - Large |  |  | 1084 | N | HOURS
|  |  | Office - Small |  |  | 882 | N | HOURS
|  |  | Restaurant |  |  | 1249 | N | HOURS
|  |  | Retail - Large |  |  | 845 | N | HOURS
|  |  | Retail - Small |  |  | 780 | N | HOURS
|  |  | Warehouse |  |  | 864 | N | HOURS
|  |  | Convenience |  |  | 1351 | N | HOURS
|  |  | Industrial |  |  | 1063 | N | HOURS
|  |  | Religious |  |  | 1031 | N | HOURS
|  |  | Nonresidential Average |  |  | 915 | N | HOURS
| [1000] |  |  |  |  | 1000 | N |  | Converts watts to kW
| [∆kWh] | [5 empty] | C | kWh | Calculated as above
| [CF] | Building Type | Convenience |  |  | 92.3% | N |  | Summer Peak Coincidence Factor for Cooling
|  |  | Education |  |  | 96.7%
|  |  | Grocery |  |  | 100%
|  |  | Health |  |  | 100%
|  |  | Hospital |  |  | 98.6%
|  |  | Industrial |  |  | 44.6%
|  |  | Lodging |  |  | 97.4%
|  |  | Multifamily |  |  | 100%
|  |  | Office - Large |  |  | 98.8%
|  |  | Office - Small |  |  | 100%
|  |  | Religious |  |  | 94.3%
|  |  | Restaurant |  |  | 99.6%
|  |  | Retail - Large |  |  | 87.6%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 77.9%
|  |  | Nonresidential Average |  |  | 92.3%

## Electric HVAC Tune Up Deemed
Electric HVAC Tune Up Deemed
| Measure Code: | NR-HVC-ACTU-V01-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
3
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | ΔkWH= [Capacity_Cool] / (1000 * [EER_rated]) * [EFLH] * [%Savings]
| Time of Sale Demand (ΔkW) | ΔkW = [ΔkWh] / [EFLH] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [CapacityCool] | [5 empty] | Y | Btuh | Cooling Capacity of new equipment in Btu/hr (note 1 ton = 12,000Btu/hr)
| [1000] |  |  |  |  | 1000 | N |  | Converts watts to kW
| [EER_rated] | [5 empty] | Y | EER | Rated EER of unit being tuned-up
| [EFLH] | Building Type | Education | Location | Zone 5 (Burlington) | 1073 | N | HOURS | Equivalent Full Load Hours for cooling in Existing Buildings
|  |  | Grocery |  |  | 320 | N | HOURS
|  |  | Health |  |  | 1449 | N | HOURS
|  |  | Hospital |  |  | 1792 | N | HOURS
|  |  | Lodging |  |  | 1464 | N | HOURS
|  |  | Multifamily |  |  | 1472 | N | HOURS
|  |  | Office - Large |  |  | 1141 | N | HOURS
|  |  | Office - Small |  |  | 986 | N | HOURS
|  |  | Restaurant |  |  | 1397 | N | HOURS
|  |  | Retail - Large |  |  | 846 | N | HOURS
|  |  | Retail - Small |  |  | 891 | N | HOURS
|  |  | Warehouse |  |  | 1032 | N | HOURS
|  |  | Convenience |  |  | 1477 | N | HOURS
|  |  | Industrial |  |  | 1185 | N | HOURS
|  |  | Religious |  |  | 1109 | N | HOURS
|  |  | Nonresidential Average |  |  | 1034 | N | HOURS
|  |  | Education |  | Zone 6 (Mason City) | 848 | N | HOURS
|  |  | Grocery |  |  | 221 | N | HOURS
|  |  | Health |  |  | 996 | N | HOURS
|  |  | Hospital |  |  | 1436 | N | HOURS
|  |  | Lodging |  |  | 1252 | N | HOURS
|  |  | Multifamily |  |  | 1045 | N | HOURS
|  |  | Office - Large |  |  | 843 | N | HOURS
|  |  | Office - Small |  |  | 667 | N | HOURS
|  |  | Restaurant |  |  | 937 | N | HOURS
|  |  | Retail - Large |  |  | 616 | N | HOURS
|  |  | Retail - Small |  |  | 531 | N | HOURS
|  |  | Warehouse |  |  | 539 | N | HOURS
|  |  | Convenience |  |  | 1128 | N | HOURS
|  |  | Industrial |  |  | 856 | N | HOURS
|  |  | Religious |  |  | 797 | N | HOURS
|  |  | Nonresidential Average |  |  | 669 | N | HOURS
|  |  | Education |  | Average/Unknown | 928 | N | HOURS
|  |  | Grocery |  |  | 356 | N | HOURS
|  |  | Health |  |  | 1207 | N | HOURS
|  |  | Hospital |  |  | 1662 | N | HOURS
|  |  | Lodging |  |  | 1460 | N | HOURS
|  |  | Multifamily |  |  | 1349 | N | HOURS
|  |  | Office - Large |  |  | 1084 | N | HOURS
|  |  | Office - Small |  |  | 882 | N | HOURS
|  |  | Restaurant |  |  | 1249 | N | HOURS
|  |  | Retail - Large |  |  | 845 | N | HOURS
|  |  | Retail - Small |  |  | 780 | N | HOURS
|  |  | Warehouse |  |  | 864 | N | HOURS
|  |  | Convenience |  |  | 1351 | N | HOURS
|  |  | Industrial |  |  | 1063 | N | HOURS
|  |  | Religious |  |  | 1031 | N | HOURS
|  |  | Nonresidential Average |  |  | 915 | N | HOURS
| [%Savings] | Tune up Component | Correct Refrigerant Charge |  |  | 2% | N | Percentage | Deemed percent savings per Tune-Up component. These are additive multiple components are performed (total provided below
|  |  | Clean condenser coils |  |  | 1% | N
|  |  | Clean evaporator coils |  |  | 1% | N
|  |  | If full tune up performed |  |  | 5% | N
| [∆kWh] | [5 empty] | C | kWh | Calculated as above
| [CF] | Building Type | Convenience |  |  | 92.3% | N |  | Summer Peak Coincidence Factor for Cooling
|  |  | Education |  |  | 96.7%
|  |  | Grocery |  |  | 100%
|  |  | Health |  |  | 100%
|  |  | Hospital |  |  | 98.6%
|  |  | Industrial |  |  | 44.6%
|  |  | Lodging |  |  | 97.4%
|  |  | Multifamily |  |  | 100%
|  |  | Office - Large |  |  | 98.8%
|  |  | Office - Small |  |  | 100%
|  |  | Religious |  |  | 94.3%
|  |  | Restaurant |  |  | 99.6%
|  |  | Retail - Large |  |  | 87.6%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 77.9%
|  |  | Nonresidential Average |  |  | 92.3%

## CFL - Standard
CFL - Standard
| Measure Code: | NR-LTG-STCFL-V01-170101
Note: This measure is effective until 12/31/2017. It should not be used beyond that date but is left in the manual for reference purposes.
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
| Building Type | Convenience | 2.1598
|  | Education | 3
|  | Grocery | 2.1445
|  | Health | 2.6274
|  | Hospital | 1.5337
|  | Industrial | 3
|  | Lodging | 3
|  | Multifamily | 3
|  | Office - Large | 3
|  | Office - Small | 3
|  | Religious | 3
|  | Restaurant | 1.8372
|  | Retail - Large | 2.46
|  | Retail - Small | 2.7071
|  | Warehouse | 3
|  | Nonresidential Average | 3
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Program Type | Retail TOS | Lumens | < 2000 lumens | 1.03
|  |  |  | > 2000 lumens | 2.76
|  | Direct Install |  | < 2000 lumens | 13.2
|  |  |  | ≥ 2000 lumens | 16.2
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
| Building Type | Convenience | 0.91 | $2.17 for bulbs <2,000 lumens $3.44 for bulbs ≥2,000 lumens
|  | Education | 2.24
|  | Grocery | 0.9
|  | Health | 1.1
|  | Hospital | 0.64
|  | Industrial | 1.47
|  | Lodging | 1.37
|  | Multifamily | 1.37
|  | Office - Large | 1.44
|  | Office - Small | 1.44
|  | Religious | 1.74
|  | Restaurant | 0.77
|  | Retail - Large | 1.03
|  | Retail - Small | 1.14
|  | Warehouse | 1.44
|  | Nonresidential Average | 1.37
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([WattsBase] - [WattsEE]) / [1,000] * [Hours] * [WHFe] * [ISR]
| Time of Sale Demand (ΔkW) | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [WHFd] * [CF]
| Time of Sale Gas (ΔTherms) | = ([WattsBase] - [WattsEE]) / [1,000] * [ ISR] * [Hours] *(- [IFTherms])
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] * (-[IFkWh])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Lumen Range | 250-309 |  |  | 19 | Y | Watts | Actual (if retrofit) or based on lumens of CFL bulb installed
|  |  | 310-749 |  |  | 23
|  |  | 750-1049 |  |  | 33.9
|  |  | 1050-1489 |  |  | 42.5
|  |  | 1490-2600 |  |  | 57.5
|  |  | 2601-3000 |  |  | 117.4
|  |  | 3001-3999 |  |  | 156.2
|  |  | 4000-6000 |  |  | 230.1
| [WattsEE] | Lumen Range | 250-309 |  |  | 5.1 | Y | Watts | Actual wattage of CFL purchased or installed
|  |  | 310-749 |  |  | 9.4
|  |  | 750-1049 |  |  | 13.4
|  |  | 1050-1489 |  |  | 18.9
|  |  | 1490-2600 |  |  | 24.8
|  |  | 2601-3000 |  |  | 41.1
|  |  | 3001-3999 |  |  | 53.8
|  |  | 4000-6000 |  |  | 65
| [Hours] | Building Type | Convenience |  |  | 4630 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Education |  |  | 1877
|  |  | Grocery |  |  | 4663
|  |  | Health |  |  | 3806
|  |  | Hospital |  |  | 6520
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3061
|  |  | Multifamily |  |  | 3061
|  |  | Office - Large |  |  | 2920
|  |  | Office - Small |  |  | 2920
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 5443
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 3694
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 3065
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [WHFe] | Building Type | Convenience |  |  | 1.14 | N | Hours | Waste heat factors for energy to account for cooling energy savings from efficient lighting
|  |  | Education |  |  | 1.07
|  |  | Grocery |  |  | 1.02
|  |  | Health |  |  | 1.09
|  |  | Hospital |  |  | 1.16
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.23
|  |  | Multifamily |  |  | 1.13
|  |  | Office - Large |  |  | 1.17
|  |  | Office - Small |  |  | 1.1
|  |  | Religious |  |  | 1.12
|  |  | Restaurant |  |  | 1
|  |  | Retail - Large |  |  | 1
|  |  | Retail - Small |  |  | 1.09
|  |  | Warehouse |  |  | 1
|  |  | Nonresidential Average |  |  | 1.06
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [ISR] | Program | Retail (Time of Sale) |  |  | 95% | Y |  | In Service Rate or the percentage of units that get installed
|  |  | Direct Install and Retrofit |  |  | 97%
| [ΔkWhheatpenalty] | [5 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Convenience | Heating Type | Resistance | 0.36 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Education |  |  | 0.45
|  |  | Grocery |  |  | 0.3
|  |  | Health |  |  | 0.35
|  |  | Hospital |  |  | 0.18
|  |  | Industrial |  |  | 0.37
|  |  | Lodging |  |  | 0.19
|  |  | Multifamily |  |  | 0.44
|  |  | Office - Large |  |  | 0.29
|  |  | Office - Small |  |  | 0.33
|  |  | Religious |  |  | 0.46
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.36
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.24
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
|  |  | Convenience |  | Heat Pump | 0.16
|  |  | Education |  |  | 0.2
|  |  | Grocery |  |  | 0.13
|  |  | Health |  |  | 0.15
|  |  | Hospital |  |  | 0.08
|  |  | Industrial |  |  | 0.16
|  |  | Lodging |  |  | 0.08
|  |  | Multifamily |  |  | 0.19
|  |  | Office - Large |  |  | 0.13
|  |  | Office - Small |  |  | 0.15
|  |  | Religious |  |  | 0.2
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.16
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.1
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [WHFd] | Building Type | Convenience |  |  | 1.31 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Education |  |  | 1.48
|  |  | Grocery |  |  | 1.2
|  |  | Health |  |  | 1.69
|  |  | Hospital |  |  | 1.26
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.47
|  |  | Multifamily |  |  | 1.15
|  |  | Office - Large |  |  | 1.04
|  |  | Office - Small |  |  | 1.28
|  |  | Religious |  |  | 1.32
|  |  | Restaurant |  |  | 1.47
|  |  | Retail - Large |  |  | 1.28
|  |  | Retail - Small |  |  | 1.2
|  |  | Warehouse |  |  | 1.19
|  |  | Nonresidential Average |  |  | 1.28
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [CF] | Building Type | Convenience |  |  | 100% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Education |  |  | 65.27%
|  |  | Grocery |  |  | 82.11%
|  |  | Health |  |  | 67%
|  |  | Hospital |  |  | 55.95%
|  |  | Industrial |  |  | 91.8%
|  |  | Lodging |  |  | 61.07%
|  |  | Multifamily |  |  | 71.17%
|  |  | Office - Large |  |  | 60.2%
|  |  | Office - Small |  |  | 51.79%
|  |  | Religious |  |  | 66%
|  |  | Restaurant |  |  | 100%
|  |  | Retail - Large |  |  | 100%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 61.8%
|  |  | Nonresidential Average |  |  | 69.07%
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [IFTherms] | Building Type | Convenience |  |  | 0.015 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Education |  |  | 0.19
|  |  | Grocery |  |  | 0.013
|  |  | Health |  |  | 0.015
|  |  | Hospital |  |  | 0.008
|  |  | Industrial |  |  | 0.016
|  |  | Lodging |  |  | 0.008
|  |  | Multifamily |  |  | 0.019
|  |  | Office - Large |  |  | 0.013
|  |  | Office - Small |  |  | 0.014
|  |  | Religious |  |  | 0.02
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.015
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.01
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [ΔTherms] | [5 empty] | C | Therms | Therm impact calculated above
| [HeatDays] |  |  |  |  | 197 | N | Days | Heat season days per year

## CFL - Specialty
CFL - Specialty
| Measure Code: | NR-LTG-SPCFL-V01-170101
Note: This measure is effective until 12/31/2017. It should not be used beyond that date but is left in the manual for reference purposes.
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
| Building Type | Convenience | 2.1598
|  | Education | 5.3277
|  | Grocery | 2.1445
|  | Health | 2.6274
|  | Hospital | 1.5337
|  | Industrial | 3.5088
|  | Lodging | 3.2669
|  | Multifamily | 3.2669
|  | Office - Large | 3.4247
|  | Office - Small | 3.4247
|  | Religious | 4.1459
|  | Restaurant | 1.8372
|  | Retail - Large | 2.46
|  | Retail - Small | 2.7071
|  | Warehouse | 3.4247
|  | Nonresidential Average | 3.2626
| Measure Cost: | [8 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Direct Install) |  |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Bulb Type | Directional | CFL Wattage | < 20W | 0.56 | 17.84
|  |  |  | ≥20W | -1.25 | 19.31
|  | Decorative and Globes |  | <15W | 3.08 | 17.8
|  |  |  | ≥15W | 2.61 | 18.15
|  | Other / Unknown |  |  | 1.81 | 17.82
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable 2 Input | Dependent Variable 2 Options | Life of Component | Cost
| Building Type | Convenience | Bulb Type | Directional | 0.93 | $7.28 for < 20W, $10.56 for ≥20W
|  | Education |  |  | 2.29
|  | Grocery |  |  | 0.92
|  | Health |  |  | 1.13
|  | Hospital |  |  | 0.66
|  | Industrial |  |  | 1.51
|  | Lodging |  |  | 1.4
|  | Multifamily |  |  | 1.4
|  | Office - Large |  |  | 1.47
|  | Office - Small |  |  | 1.47
|  | Religious |  |  | 1.78
|  | Restaurant |  |  | 0.79
|  | Retail - Large |  |  | 1.06
|  | Retail - Small |  |  | 1.16
|  | Warehouse |  |  | 1.47
|  | Nonresidential Average |  |  | 1.4
|  | Convenience |  | Decorative/Globe | 0.71 | $4.73 for <15W, $5.54 for ≥15W
|  | Education |  |  | 1.76
|  | Grocery |  |  | 0.71
|  | Health |  |  | 0.87
|  | Hospital |  |  | 0.51
|  | Industrial |  |  | 1.16
|  | Lodging |  |  | 1.08
|  | Multifamily |  |  | 1.08
|  | Office - Large |  |  | 1.13
|  | Office - Small |  |  | 1.13
|  | Religious |  |  | 1.37
|  | Restaurant |  |  | 0.61
|  | Retail - Large |  |  | 0.81
|  | Retail - Small |  |  | 0.89
|  | Warehouse |  |  | 1.13
|  | Nonresidential Average |  |  | 1.08
|  | Convenience |  | Unknown | 0.82 | 6.01
|  | Education |  |  | 2.02
|  | Grocery |  |  | 0.81
|  | Health |  |  | 1
|  | Hospital |  |  | 0.58
|  | Industrial |  |  | 1.33
|  | Lodging |  |  | 1.24
|  | Multifamily |  |  | 1.24
|  | Office - Large |  |  | 1.3
|  | Office - Small |  |  | 1.3
|  | Religious |  |  | 1.58
|  | Restaurant |  |  | 0.7
|  | Retail - Large |  |  | 0.93
|  | Retail - Small |  |  | 1.03
|  | Warehouse |  |  | 1.3
|  | Nonresidential Average |  |  | 1.24
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([WattsBase] - [WattsEE]) / [1,000] * [Hours] * [WHFe] * [ISR]
| Time of Sale Demand (ΔkW) | =([WattsBase[ - [WattsEE]) / [1,000] * [ISR] * [WHFd] * [CF]
| Time of Sale Gas (ΔTherms) | = ([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] * (- [IFTherms])
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] * (-[IFkWh])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Bulb Type (EISA Exempt) | 3-way | Lumen range | 250-449 | 21.3 | N | Watts | Based on lumens of CFL bulb installed and includes blend of incandescent/halogen , CFL and LED by weightings provided in table below . Note that when an IA net-to-gross (NTG) factor is determined for this measure, this blended baseline should be replaced with the Incandescent/Halogen baseline only.
[5 empty] | 450-799 | 34.3
[5 empty] | 800-1099 | 50.3
[5 empty] | 1100-1599 | 63.4
[5 empty] | 1600-1999 | 84.5
[5 empty] | 2000-2549 | 106.7
[5 empty] | 2550-2999 | 128.3
|  |  | Globe (medium and intermediate bases less than 750 lumens) |  | 90-179 | 8.6
[5 empty] | 180-249 | 13
[5 empty] | 250-349 | 21.1
[5 empty] | 350-749 | 33.6
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) |  | 70-89 | 8.4
[5 empty] | 90-149 | 12.5
[5 empty] | 150-299 | 20.9
[5 empty] | 300-749 | 33.3
|  |  | Globe (candelabra bases less than 1050 lumens) |  | 90-179 | 8.6
[5 empty] | 180-249 | 13
[5 empty] | 250-349 | 21.1
[5 empty] | 350-499 | 33.4
[5 empty] | 500-1049 | 50.2
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra bases less than 1050 lumens) |  | 70-89 | 8.4
[5 empty] | 90-149 | 12.5
[5 empty] | 150-299 | 20.8
[5 empty] | 300-499 | 33.2
[5 empty] | 500-1049 | 50.2
|  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) |  | 420-472 | 33.9
[5 empty] | 473-524 | 38
[5 empty] | 525-714 | 42.4
[5 empty] | 715-937 | 54.8
[5 empty] | 938-1259 | 63.7
[5 empty] | 1260-1399 | 76.1
[5 empty] | 1400-1739 | 85.1
[5 empty] | 1740-2174 | 102.5
[5 empty] | 2175-2624 | 127.7
[5 empty] | 2625-2999 | 151.2
[5 empty] | 3000-4500 | 175
|  |  | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" |  | 400-449 | 33.7
[5 empty] | 450-499 | 37.9
[5 empty] | 500-649 | 42.2
[5 empty] | 650-1199 | 55.2
|  |  | *ER30, BR30, BR40, or ER40 |  | 400-449 | 34.1
[5 empty] | 450-499 | 38.4
[5 empty] | 500-649 | 42.6
|  |  | BR30, BR40, or ER40 |  | 650-1419 | 55
|  |  | R20 |  | 400-449 | 34.1
[5 empty] | 450-719 | 38
|  |  | *All reflector lamps below lumen ranges specified above |  | 200-299 | 17
[5 empty] | 300-399 | 25.5
|  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) |  | 250-309 | 20.9
[5 empty] | 310-749 | 24.8
[5 empty] | 750-1049 | 36.8
[5 empty] | 1050-1489 | 45.6
[5 empty] | 1490-2600 | 61.8
| [WattsEE] | Bulb Type (EISA Exempt) | 3-way | Lumen range | 250-449 | 6.4 | Y | Watts | Actual wattage of energy efficient specialty bulb purchased, if unknown, assume the following defaults
[5 empty] | 450-799 | 11.4
[5 empty] | 800-1099 | 13
[5 empty] | 1100-1599 | 20.8
[5 empty] | 1600-1999 | 26
[5 empty] | 2000-2549 | 32.2
[5 empty] | 2550-2999 | 40
|  |  | Globe (medium and intermediate bases less than 750 lumens) |  | 90-179 | 3
[5 empty] | 180-249 | 4.8
[5 empty] | 250-349 | 6.7
[5 empty] | 350-749 | 9.9
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) |  | 70-89 | 1.8
[5 empty] | 90-149 | 2.7
[5 empty] | 150-299 | 5
[5 empty] | 300-749 | 7.5
|  |  | Globe (candelabra bases less than 750 lumens) |  | 90-179 | 3
[5 empty] | 180-249 | 4.8
[5 empty] | 250-349 | 6.7
[5 empty] | 350-499 | 9.4
[5 empty] | 500-1049 | 15.5
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra 1050 lumens) |  | 70-89 | 1.8
[5 empty] | 90-149 | 2.7
[5 empty] | 150-299 | 5
[5 empty] | 300-499 | 7.7
[5 empty] | 500-1049 | 15.5
|  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) |  | 420-472 | 11
[5 empty] | 473-524 | 12.5
[5 empty] | 525-714 | 14.9
[5 empty] | 715-937 | 15.6
[5 empty] | 938-1259 | 21.1
[5 empty] | 1260-1399 | 23
[5 empty] | 1400-1739 | 31.4
[5 empty] | 1740-2174 | 39.1
[5 empty] | 2175-2624 | 48
[5 empty] | 2625-2999 | 56.2
[5 empty] | 3000-4500 | 75
|  |  | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" |  | 400-449 | 10.6
[5 empty] | 450-499 | 11.9
[5 empty] | 500-649 | 14.4
[5 empty] | 650-1199 | 18.5
|  |  | *ER30, BR30, BR40, or ER40 |  | 400-449 | 10.6
[5 empty] | 450-499 | 11.9
[5 empty] | 500-649 | 14.4
|  |  | BR30, BR40, or ER 40 |  | 650-1419 | 18
|  |  | R20 |  | 400-449 | 10.6
[5 empty] | 450-719 | 12.5
|  |  | *All reflector lamps below lumen ranges specified above |  | 200-299 | 6.2
[5 empty] | 300-399 | 8.7
|  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) |  | 250-309 | 5.1
[5 empty] | 310-749 | 9.5
[5 empty] | 750-1049 | 13.5
[5 empty] | 1050-1489 | 18.9
[5 empty] | 1490-2600 | 24.8
| [ISR] | Program | Retail (Time of Sale) |  |  | 95% | Y |  | In Service Rate or the percentage of units that get installed
|  |  | Direct Install and Retrofit |  |  | 97%
| [Hours] | Building Type | Convenience |  |  | 4630 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Education |  |  | 1877
|  |  | Grocery |  |  | 4663
|  |  | Health |  |  | 3806
|  |  | Hospital |  |  | 6520
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3061
|  |  | Multifamily |  |  | 3061
|  |  | Office - Large |  |  | 2920
|  |  | Office - Small |  |  | 2920
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 5443
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 3694
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 3065
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [WHFe] | Building Type | Convenience |  |  | 1.14 | N | Hours | Waste heat factors for energy to account for cooling energy savings from efficient lighting
|  |  | Education |  |  | 1.07
|  |  | Grocery |  |  | 1.02
|  |  | Health |  |  | 1.09
|  |  | Hospital |  |  | 1.16
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.23
|  |  | Multifamily |  |  | 1.13
|  |  | Office - Large |  |  | 1.17
|  |  | Office - Small |  |  | 1.1
|  |  | Religious |  |  | 1.12
|  |  | Restaurant |  |  | 1
|  |  | Retail - Large |  |  | 1
|  |  | Retail - Small |  |  | 1.09
|  |  | Warehouse |  |  | 1
|  |  | Nonresidential Average |  |  | 1.06
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [ΔkWhheatpenalty] | [5 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Convenience | Heating Type | Resistance | 0.36 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Education |  |  | 0.45
|  |  | Grocery |  |  | 0.3
|  |  | Health |  |  | 0.35
|  |  | Hospital |  |  | 0.18
|  |  | Industrial |  |  | 0.37
|  |  | Lodging |  |  | 0.19
|  |  | Multifamily |  |  | 0.44
|  |  | Office - Large |  |  | 0.29
|  |  | Office - Small |  |  | 0.33
|  |  | Religious |  |  | 0.46
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.36
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.24
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
|  |  | Convenience |  | Heat Pump | 0.16
|  |  | Education |  |  | 0.2
|  |  | Grocery |  |  | 0.13
|  |  | Health |  |  | 0.15
|  |  | Hospital |  |  | 0.08
|  |  | Industrial |  |  | 0.16
|  |  | Lodging |  |  | 0.08
|  |  | Multifamily |  |  | 0.19
|  |  | Office - Large |  |  | 0.13
|  |  | Office - Small |  |  | 0.15
|  |  | Religious |  |  | 0.2
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.16
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.1
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [WHFd] | Building Type | Convenience |  |  | 1.31 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Education |  |  | 1.48
|  |  | Grocery |  |  | 1.2
|  |  | Health |  |  | 1.69
|  |  | Hospital |  |  | 1.26
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.47
|  |  | Multifamily |  |  | 1.15
|  |  | Office - Large |  |  | 1.04
|  |  | Office - Small |  |  | 1.28
|  |  | Religious |  |  | 1.32
|  |  | Restaurant |  |  | 1.47
|  |  | Retail - Large |  |  | 1.28
|  |  | Retail - Small |  |  | 1.2
|  |  | Warehouse |  |  | 1.19
|  |  | Nonresidential Average |  |  | 1.28
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [CF] | Building Type | Convenience |  |  | 100% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Education |  |  | 65.27%
|  |  | Grocery |  |  | 82.11%
|  |  | Health |  |  | 67%
|  |  | Hospital |  |  | 55.95%
|  |  | Industrial |  |  | 91.8%
|  |  | Lodging |  |  | 61.07%
|  |  | Multifamily |  |  | 71.17%
|  |  | Office - Large |  |  | 60.2%
|  |  | Office - Small |  |  | 51.79%
|  |  | Religious |  |  | 66%
|  |  | Restaurant |  |  | 100%
|  |  | Retail - Large |  |  | 100%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 61.8%
|  |  | Nonresidential Average |  |  | 69.07%
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [IFTherms] | Building Type | Convenience |  |  | 0.015 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Education |  |  | 0.19
|  |  | Grocery |  |  | 0.013
|  |  | Health |  |  | 0.015
|  |  | Hospital |  |  | 0.008
|  |  | Industrial |  |  | 0.016
|  |  | Lodging |  |  | 0.008
|  |  | Multifamily |  |  | 0.019
|  |  | Office - Large |  |  | 0.013
|  |  | Office - Small |  |  | 0.014
|  |  | Religious |  |  | 0.02
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.015
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.01
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [ΔTherms] | [5 empty] | C | Therms | Therm impact calculated above
| [HeatDays] |  |  |  |  | 197 | N | Days | Heat season days per year

## LED Lamp - Standard
LED Lamp - Standard
| Measure Code: | NR-LTG-LEDA-V05-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
| Building Type | Agricultural Animal Housing and Warehousing | 6.9281
|  | Convenience | 4.3693
|  | Education | 10.7778
|  | Exterior Lighting | 4.3263
|  | Grocery | 4.3384
|  | Health | 5.3153
|  | Hospital | 3.1028
|  | Industrial | 7.0982
|  | Lodging | 6.609
|  | Multifamily | 6.609
|  | Office - Large | 6.9281
|  | Office - Small | 6.9281
|  | Religious | 8.3872
|  | Restaurant | 3.7167
|  | Retail - Large | 4.9766
|  | Retail - Small | 5.4764
|  | Warehouse | 6.9281
|  | Nonresidential Average | 6.6003
|  | Unconditioned building | As specific building above
|  | Refrigerated Cases | As specific building above
|  | Freezer Cases | As specific building above
| Measure Cost: | [9 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Incremental Cost | Full Cost (Early Replacement) |  |  | Dependent Variable Input 1
| Costs known? | Known |  |  |  |  | Actual
|  | Unknown | CRI | <90 | Product Type | ENERGY STAR | 0.77
[6 empty] | CEE Tier 2 | 0.9
|  |  |  | >=90 |  | ENERGY STAR | 0.99
[6 empty] | CEE Tier 2 | 1.07
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Dependent Variable Input 4 | Dependent Variable 4 Options | Life of Component | Cost
| CRI | <90 | [6 empty] | 1 | 1.07
|  | >=90 | [6 empty] | 1 | 1.08
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =(([WattsBase] - [WattsEE]) / [1,000] * [Hours] * [WHFe] * [ISR]) * [MidLifeAdj]
| Time of Sale Demand (ΔkW) | =(([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [WHFd] * [CF]) * [MidLifeAdj]
| Time of Sale Gas (ΔTherms) | = (([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] *(- [IFTherms])) * [MidLifeAdj]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] * (-[IFkWh])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Watts_Base] | Lumen Range | 250-309 |  |  |  |  | 12.8 | N | Watts | Actual (if retrofit) or based on lumens of LED bulb installed
|  |  | 310-749 |  |  |  |  | 16.5
|  |  | 750-1049 |  |  |  |  | 25.3
|  |  | 1050-1489 |  |  |  |  | 32.4
|  |  | 1490-2600 |  |  |  |  | 46.5
|  |  | 2601-3000 |  |  |  |  | 86.8
|  |  | 3001-3999 |  |  |  |  | 113.6
|  |  | 4000-6000 |  |  |  |  | 166.8
|  |  | Unknown |  |  |  |  | 27.1
| [WattsEE] | Product Type | ENERGY STAR | CRI | <90 | Lumen Range | 250-309 | 3.5 | Y | Watts | Actual wattage of LED purchased or installed
[7 empty] | 310-749 | 6.6
[7 empty] | 750-1049 | 11.2
[7 empty] | 1050-1489 | 15.9
[7 empty] | 1490-2600 | 25.6
[7 empty] | 2601-3300 | 36.9
[7 empty] | 3301-3999 | 45.6
[7 empty] | 4000-6000 | 62.5
[5 empty] | >=90 |  | 250-309 | 4
[7 empty] | 310-749 | 7.6
[7 empty] | 750-1049 | 12.9
[7 empty] | 1050-1489 | 18.1
[7 empty] | 1490-2600 | 29.2
[7 empty] | 2601-3300 | 42.2
[7 empty] | 3301-3999 | 52.1
[7 empty] | 4000-6000 | 71.4
|  |  | CEE Tier 2 |  | <90 |  | 250-309 | 2.9
[7 empty] | 310-749 | 5.6
[7 empty] | 750-1049 | 9.5
[7 empty] | 1050-1489 | 13.4
[7 empty] | 1490-2600 | 21.5
[7 empty] | 2601-3300 | 31.1
[7 empty] | 3301-3999 | 38.4
[7 empty] | 4000-6000 | 52.6
[5 empty] | >=90 |  | 250-309 | 3.5
[7 empty] | 310-749 | 6.6
[7 empty] | 750-1049 | 11.2
[7 empty] | 1050-1489 | 15.9
[7 empty] | 1490-2600 | 25.6
[7 empty] | 2601-3300 | 36.9
[7 empty] | 3301-3999 | 45.6
[7 empty] | 4000-6000 | 62.5
|  | Unknown | [5 empty] | 12.4
| [Hours] | Building Type | Agricultural Animal Housing and Warehousing |  |  |  |  | 2920 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Convenience |  |  |  |  | 4630
|  |  | Education |  |  |  |  | 1877
|  |  | Exterior Lighting |  |  |  |  | 4676
|  |  | Grocery |  |  |  |  | 4663
|  |  | Health |  |  |  |  | 3806
|  |  | Hospital |  |  |  |  | 6520
|  |  | Industrial |  |  |  |  | 2850
|  |  | Lodging |  |  |  |  | 3061
|  |  | Multifamily |  |  |  |  | 3061
|  |  | Office - Large |  |  |  |  | 2920
|  |  | Office - Small |  |  |  |  | 2920
|  |  | Religious |  |  |  |  | 2412
|  |  | Restaurant |  |  |  |  | 5443
|  |  | Retail - Large |  |  |  |  | 4065
|  |  | Retail - Small |  |  |  |  | 3694
|  |  | Warehouse |  |  |  |  | 2920
|  |  | Nonresidential Average |  |  |  |  | 3065
|  |  | Unconditioned building |  |  |  |  | As specific building above
|  |  | Refrigerated Cases |  |  |  |  | As specific building above
|  |  | Freezer Cases |  |  |  |  | As specific building above
| [WHFe] | Building Type | Agricultural Animal Housing and Warehousing |  |  |  |  | 1 | N |  | Waste heat factors for energy to account for cooling energy savings from efficient lighting
|  |  | Convenience |  |  |  |  | 1.14
|  |  | Education |  |  |  |  | 1.07
|  |  | Exterior Lighting |  |  |  |  | 1
|  |  | Grocery |  |  |  |  | 1.02
|  |  | Health |  |  |  |  | 1.09
|  |  | Hospital |  |  |  |  | 1.16
|  |  | Industrial |  |  |  |  | 1.02
|  |  | Lodging |  |  |  |  | 1.23
|  |  | Multifamily |  |  |  |  | 1.13
|  |  | Office - Large |  |  |  |  | 1.17
|  |  | Office - Small |  |  |  |  | 1.1
|  |  | Religious |  |  |  |  | 1.12
|  |  | Restaurant |  |  |  |  | 1
|  |  | Retail - Large |  |  |  |  | 1
|  |  | Retail - Small |  |  |  |  | 1.09
|  |  | Warehouse |  |  |  |  | 1
|  |  | Nonresidential Average |  |  |  |  | 1.06
|  |  | Unconditioned building |  |  |  |  | 1
|  |  | Refrigerated Cases |  |  |  |  | 1.29
|  |  | Freezer Cases |  |  |  |  | 1.5
| [ISR] | Program | Retail (Time of Sale) |  |  |  |  | 89% | Y |  | In Service Rate or the percentage of units that get installed
|  |  | Direct Install and Retrofit |  |  |  |  | 97%
| [MidLifeAdj] | Year and Type | Before 2025 |  |  |  |  | 100% | N | Percentage | Mid Life Adjustment to account for baseline shifting within the measure life to a CFL in 2020. This factor should be applied to the annual savings for years 2021 onwards for any measure installed prior to 2021.
|  |  | 2025 on | Efficiency | ENERGY STAR |  |  | 45%
[5 empty] | CEE T2 |  |  | 51%
| [ΔkWhheatpenalty] | [7 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Agricultural Animal Housing and Warehousing | Heating Type | Resistance |  |  | 0 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Convenience |  |  |  |  | 0.36
|  |  | Education |  |  |  |  | 0.45
|  |  | Exterior Lighting |  |  |  |  | 0
|  |  | Grocery |  |  |  |  | 0.3
|  |  | Health |  |  |  |  | 0.35
|  |  | Hospital |  |  |  |  | 0.18
|  |  | Industrial |  |  |  |  | 0.37
|  |  | Lodging |  |  |  |  | 0.19
|  |  | Multifamily |  |  |  |  | 0.44
|  |  | Office - Large |  |  |  |  | 0.29
|  |  | Office - Small |  |  |  |  | 0.33
|  |  | Religious |  |  |  |  | 0.46
|  |  | Restaurant |  |  |  |  | 0
|  |  | Retail - Large |  |  |  |  | 0
|  |  | Retail - Small |  |  |  |  | 0.36
|  |  | Warehouse |  |  |  |  | 0
|  |  | Nonresidential Average |  |  |  |  | 0.24
|  |  | Unconditioned building |  |  |  |  | 0
|  |  | Refrigerated Cases |  |  |  |  | 0
|  |  | Freezer Cases |  |  |  |  | 0
|  |  | Agricultural Animal Housing and Warehousing |  | Heat Pump |  |  | 0
|  |  | Convenience |  |  |  |  | 0.16
|  |  | Education |  |  |  |  | 0.2
|  |  | Exterior Lighting |  |  |  |  | 0
|  |  | Grocery |  |  |  |  | 0.13
|  |  | Health |  |  |  |  | 0.15
|  |  | Hospital |  |  |  |  | 0.08
|  |  | Industrial |  |  |  |  | 0.16
|  |  | Lodging |  |  |  |  | 0.08
|  |  | Multifamily |  |  |  |  | 0.19
|  |  | Office - Large |  |  |  |  | 0.13
|  |  | Office - Small |  |  |  |  | 0.15
|  |  | Religious |  |  |  |  | 0.2
|  |  | Restaurant |  |  |  |  | 0
|  |  | Retail - Large |  |  |  |  | 0
|  |  | Retail - Small |  |  |  |  | 0.16
|  |  | Warehouse |  |  |  |  | 0
|  |  | Nonresidential Average |  |  |  |  | 0.1
|  |  | Unconditioned building |  |  |  |  | 0
|  |  | Refrigerated Cases |  |  |  |  | 0
|  |  | Freezer Cases |  |  |  |  | 0
| [WHFd] | Building Type | Agricultural Animal Housing and Warehousing |  |  |  |  | 1 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Convenience |  |  |  |  | 1.31
|  |  | Education |  |  |  |  | 1.48
|  |  | Exterior Lighting |  |  |  |  | 1
|  |  | Grocery |  |  |  |  | 1.2
|  |  | Health |  |  |  |  | 1.69
|  |  | Hospital |  |  |  |  | 1.26
|  |  | Industrial |  |  |  |  | 1.02
|  |  | Lodging |  |  |  |  | 1.47
|  |  | Multifamily |  |  |  |  | 1.15
|  |  | Office - Large |  |  |  |  | 1.04
|  |  | Office - Small |  |  |  |  | 1.28
|  |  | Religious |  |  |  |  | 1.32
|  |  | Restaurant |  |  |  |  | 1.47
|  |  | Retail - Large |  |  |  |  | 1.28
|  |  | Retail - Small |  |  |  |  | 1.2
|  |  | Warehouse |  |  |  |  | 1.19
|  |  | Nonresidential Average |  |  |  |  | 1.28
|  |  | Unconditioned building |  |  |  |  | 1
|  |  | Refrigerated Cases |  |  |  |  | 1.29
|  |  | Freezer Cases |  |  |  |  | 1.5
| [CF] | Building Type | Agricultural Animal Housing and Warehousing |  |  |  |  | 61.8% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Convenience |  |  |  |  | 100%
|  |  | Education |  |  |  |  | 65.27%
|  |  | Exterior Lighting |  |  |  |  | 0%
|  |  | Grocery |  |  |  |  | 82.11%
|  |  | Health |  |  |  |  | 67%
|  |  | Hospital |  |  |  |  | 55.95%
|  |  | Industrial |  |  |  |  | 91.8%
|  |  | Lodging |  |  |  |  | 61.07%
|  |  | Multifamily |  |  |  |  | 71.17%
|  |  | Office - Large |  |  |  |  | 60.2%
|  |  | Office - Small |  |  |  |  | 51.79%
|  |  | Religious |  |  |  |  | 66%
|  |  | Restaurant |  |  |  |  | 100%
|  |  | Retail - Large |  |  |  |  | 100%
|  |  | Retail - Small |  |  |  |  | 100%
|  |  | Warehouse |  |  |  |  | 61.8%
|  |  | Nonresidential Average |  |  |  |  | 69.07%
|  |  | Unconditioned building |  |  |  |  | As specific building above
|  |  | Refrigerated Cases |  |  |  |  | As specific building above
|  |  | Freezer Cases |  |  |  |  | As specific building above
| [IFTherms] | Building Type | Agricultural Animal Housing and Warehousing |  |  |  |  | 0 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Convenience |  |  |  |  | 0.015
|  |  | Education |  |  |  |  | 0.019
|  |  | Exterior Lighting |  |  |  |  | 0
|  |  | Grocery |  |  |  |  | 0.013
|  |  | Health |  |  |  |  | 0.015
|  |  | Hospital |  |  |  |  | 0.008
|  |  | Industrial |  |  |  |  | 0.016
|  |  | Lodging |  |  |  |  | 0.008
|  |  | Multifamily |  |  |  |  | 0.019
|  |  | Office - Large |  |  |  |  | 0.013
|  |  | Office - Small |  |  |  |  | 0.014
|  |  | Religious |  |  |  |  | 0.02
|  |  | Restaurant |  |  |  |  | 0
|  |  | Retail - Large |  |  |  |  | 0
|  |  | Retail - Small |  |  |  |  | 0.015
|  |  | Warehouse |  |  |  |  | 0
|  |  | Nonresidential Average |  |  |  |  | 0.01
|  |  | Unconditioned building |  |  |  |  | 0
|  |  | Refrigerated Cases |  |  |  |  | 0
|  |  | Freezer Cases |  |  |  |  | 0
| [ΔTherms] | [7 empty] | C | Therms | Therm impact calculated above
| [HeatDays] | [6 empty] | 197 | N | Days | Heat season days per year

## LED Lamp - Specialty
LED Lamp - Specialty
| Measure Code: | NR-LTG-LEDS-V05-210101
| Lifetime of Efficient Equipment: | [6 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
| Building Type | Agricultural Animal Housing and Warehousing | Bulb Type | Directional | 8.576
|  | Convenience |  |  | 5.4086
|  | Education |  |  | 13.3415
|  | Exterior Lighting |  |  | 5.3554
|  | Grocery |  |  | 5.3704
|  | Health |  |  | 6.5796
|  | Hospital |  |  | 3.8408
|  | Industrial |  |  | 8.7867
|  | Lodging |  |  | 8.181
|  | Multifamily |  |  | 8.181
|  | Office - Large |  |  | 8.576
|  | Office - Small |  |  | 8.576
|  | Religious |  |  | 10.3823
|  | Restaurant |  |  | 4.6008
|  | Retail - Large |  |  | 6.1604
|  | Retail - Small |  |  | 6.7791
|  | Warehouse |  |  | 8.576
|  | Nonresidential Average |  |  | 8.1703
|  | Unconditioned building |  |  | As specific building above
|  | Refrigerated Cases |  |  | As specific building above
|  | Freezer Cases |  |  | As specific building above
|  | Agricultural Animal Housing and Warehousing |  | Decorative | 5.8661
|  | Convenience |  |  | 3.6996
|  | Education |  |  | 9.1257
|  | Exterior Lighting |  |  | 3.6632
|  | Grocery |  |  | 3.6734
|  | Health |  |  | 4.5005
|  | Hospital |  |  | 2.6271
|  | Industrial |  |  | 6.0102
|  | Lodging |  |  | 5.5959
|  | Multifamily |  |  | 5.5959
|  | Office - Large |  |  | 5.8661
|  | Office - Small |  |  | 5.8661
|  | Religious |  |  | 7.1016
|  | Restaurant |  |  | 3.147
|  | Retail - Large |  |  | 4.2138
|  | Retail - Small |  |  | 4.637
|  | Warehouse |  |  | 5.8661
|  | Nonresidential Average |  |  | 5.5886
|  | Unconditioned building |  |  | As specific building above
|  | Refrigerated Cases |  |  | As specific building above
|  | Freezer Cases |  |  | As specific building above
| Measure Cost: | [10 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Dependent Variable Input 4 | Dependent Variable 4 Options | Incremental Cost |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Costs known? | Known | [6 empty] | Actual
|  | Unknown | Bulb Type | Directional | CRI | <90 | Product Type | ENERGY STAR | 0.42
[8 empty] | CEE Tier 2 | 11.58
[6 empty] | >=90 |  | ENERGY STAR | 0.39
[8 empty] | CEE Tier 2 | 11.31
|  |  |  | Decorative |  | <90 |  | ENERGY STAR | 2.07
[8 empty] | CEE Tier 2 | 2.4
[6 empty] | >=90 |  | ENERGY STAR | 2.62
[8 empty] | CEE Tier 2 | 3
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Dependent Variable Input 4 | Dependent Variable 4 Options | Dependent Variable Input 5 | Dependent Variable 5 Options | Life of Component | Cost
| Bulb Type | Directional | CRI | <90 | [6 empty] | 1 | 2
|  |  |  | >=90 | [6 empty] | 1 | 2
|  | Decorative |  | <90 | [6 empty] | 1 | 2.5
|  |  |  | >=90 | [6 empty] | 1 | 2.52
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =(([WattsBase] - [WattsEE]) / [1,000] * [Hours] * [WHFe] * [ISR]) * [MidLifeAdj]
| Time of Sale Demand (ΔkW) | =(([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [WHFd] * [CF]) * [MidLifeAdj]
| Time of Sale Gas (ΔTherms) | = (([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] *(- [IFTherms])) * [MidLifeAdj]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] * (-[IFkWh])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Dependent Variable Input 4 | Dependent Variable 4 Options | Dependent Variable Input 5 | Dependent Variable 45Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Bulb Type (Decorative) | 3-way | Lumen range | 250-449 | [6 empty] | 14.2 | N | Watts | Based on lumens of LED'Based on lumens of LED bulb installed and includes blend of incandescent/halogen , CFL and LED by weightings provided in table below . Note that when an IA net-to-gross (NTG) factor is determined for this measure, this blended baseline should be replaced with the Incandescent/Halogen baseline only.bulb installed and includes blend of incandescent/halogen , CFL and LED by weightings provided in table below . Note that when an IA net-to-gross (NTG) factor is determined for this measure, this blended baseline should be replaced with the Incandescent/Halogen baseline only.
[5 empty] | 450-799 | [6 empty] | 23.2
[5 empty] | 800-1099 | [6 empty] | 35
[5 empty] | 1100-1599 | [6 empty] | 45
[5 empty] | 1600-1999 | [6 empty] | 60
[5 empty] | 2000-2549 | [6 empty] | 75.1
[5 empty] | 2550-2999 | [6 empty] | 90.5
|  |  | Globe (medium and intermediate bases less than 750 lumens) |  | 90-179 | [6 empty] | 5.9
[5 empty] | 180-249 | [6 empty] | 9
[5 empty] | 250-349 | [6 empty] | 14.5
[5 empty] | 350-749 | [6 empty] | 23.8
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) |  | 70-89 | [6 empty] | 5.4
[5 empty] | 90-149 | [6 empty] | 8.1
[5 empty] | 150-299 | [6 empty] | 13.7
[5 empty] | 300-749 | [6 empty] | 23.6
|  |  | Globe (candelabra bases less than 1050 lumens) |  | 90-179 | [6 empty] | 5.9
[5 empty] | 180-249 | [6 empty] | 9
[5 empty] | 250-349 | [6 empty] | 14.5
[5 empty] | 350-499 | [6 empty] | 22.6
[5 empty] | 500-1049 | [6 empty] | 35.2
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra bases less than 1050 lumens) |  | 70-89 | [6 empty] | 5.4
[5 empty] | 90-149 | [6 empty] | 8.1
[5 empty] | 150-299 | [6 empty] | 13.7
[5 empty] | 300-499 | [6 empty] | 22.4
[5 empty] | 500-1049 | [6 empty] | 35.2
|  |  | Unknown |  | Unknown | [6 empty] | 27.9
|  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) |  | 420-472 | [6 empty] | 12.4
[5 empty] | 473-524 | [6 empty] | 13.9
[5 empty] | 525-714 | [6 empty] | 16.4
[5 empty] | 715-937 | [6 empty] | 21.6
[5 empty] | 938-1259 | [6 empty] | 27
[5 empty] | 1260-1399 | [6 empty] | 32.6
[5 empty] | 1400-1739 | [6 empty] | 37.5
[5 empty] | 1740-2174 | [6 empty] | 46
[5 empty] | 2175-2624 | [6 empty] | 56.9
[5 empty] | 2625-2999 | [6 empty] | 66.5
[5 empty] | 3000-4500 | [6 empty] | 83.6
|  |  | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" |  | 400-449 | [6 empty] | 12.1
[5 empty] | 450-499 | [6 empty] | 13.6
[5 empty] | 500-649 | [6 empty] | 15.8
[5 empty] | 650-1199 | [6 empty] | 23
|  |  | *ER30, BR30, BR40, or ER40 |  | 400-449 | [6 empty] | 12.1
[5 empty] | 450-499 | [6 empty] | 13.6
[5 empty] | 500-649 | [6 empty] | 15.8
|  |  | BR30, BR40, or ER40 |  | 650-1419 | [6 empty] | 24.6
|  |  | R20 |  | 400-449 | [6 empty] | 12.1
[5 empty] | 450-719 | [6 empty] | 15.2
|  |  | *All reflector lamps below lumen ranges specified above |  | 200-299 | [6 empty] | 6.6
[5 empty] | 300-399 | [6 empty] | 9.5
|  |  | Unknown |  | Unknown | [6 empty] | 21.4
|  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) |  | 250-309 | [6 empty] | 14.3
[5 empty] | 310-749 | [6 empty] | 18.6
[5 empty] | 750-1049 | [6 empty] | 28.6
[5 empty] | 1050-1489 | [6 empty] | 36.9
[5 empty] | 1490-2600 | [6 empty] | 53.2
|  |  | Unknown |  | Unknown | [6 empty] | 30.7
| [WattsEE] | Bulb Type (Decorative) | 3-way | Product Type | ENERGY STAR | CRI | <90 | Lumen Range | 250-449 |  |  | 4.4 | Y | Watts | Actual wattage of LED pruchased/installed. If unknown, use default provided below
[9 empty] | 450-799 |  |  | 7.8
[9 empty] | 800-1099 |  |  | 11.9
[9 empty] | 1100-1599 |  |  | 16.9
[9 empty] | 1600-1999 |  |  | 22.5
[9 empty] | 2000-2549 |  |  | 28.4
[9 empty] | 2550-2999 |  |  | 34.7
|  |  | Globe (medium and intermediate bases less than 750 lumens) | [5 empty] | 90-179 |  |  | 2.1
[9 empty] | 180-249 |  |  | 3.3
[9 empty] | 250-349 |  |  | 4.6
[9 empty] | 350-749 |  |  | 8.5
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | [5 empty] | 70-89 |  |  | 1.2
[9 empty] | 90-149 |  |  | 1.8
[9 empty] | 150-299 |  |  | 3.5
[9 empty] | 300-749 |  |  | 8.1
|  |  | Globe (candelabra bases less than 750 lumens) | [5 empty] | 90-179 |  |  | 2.1
[9 empty] | 180-249 |  |  | 3.3
[9 empty] | 250-349 |  |  | 4.6
[9 empty] | 350-499 |  |  | 6.5
[9 empty] | 500-1049 |  |  | 11.9
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra 1050 lumens) | [5 empty] | 70-89 |  |  | 1.2
[9 empty] | 90-149 |  |  | 1.8
[9 empty] | 150-299 |  |  | 3.5
[9 empty] | 300-499 |  |  | 6.1
[9 empty] | 500-1049 |  |  | 11.9
|  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) | [5 empty] | 420-472 |  |  | 6.4
[9 empty] | 473-524 |  |  | 7.1
[9 empty] | 525-714 |  |  | 8.9
[9 empty] | 715-937 |  |  | 11.8
[9 empty] | 938-1259 |  |  | 15.7
[9 empty] | 1260-1399 |  |  | 19
[9 empty] | 1400-1739 |  |  | 22.4
[9 empty] | 1740-2174 |  |  | 28
[9 empty] | 2175-2624 |  |  | 34.3
[9 empty] | 2625-2999 |  |  | 40.2
[9 empty] | 3000-4500 |  |  | 53.6
|  |  | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" | [5 empty] | 400-449 |  |  | 6.1
[9 empty] | 450-499 |  |  | 6.8
[9 empty] | 500-649 |  |  | 8.2
[9 empty] | 650-1199 |  |  | 13.2
|  |  | *ER30, BR30, BR40, or ER40 | [5 empty] | 400-449 |  |  | 6.1
[9 empty] | 450-499 |  |  | 6.8
[9 empty] | 500-649 |  |  | 8.2
|  |  | BR30, BR40, or ER 40 | [5 empty] | 650-1419 |  |  | 14.8
|  |  | R20 | [5 empty] | 400-449 |  |  | 6.1
[9 empty] | 450-719 |  |  | 8.4
|  |  | *All reflector lamps below lumen ranges specified above | [5 empty] | 200-299 |  |  | 3.6
[9 empty] | 300-399 |  |  | 5
|  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) | [5 empty] | 250-309 |  |  | 3.5
[9 empty] | 310-749 |  |  | 6.6
[9 empty] | 750-1049 |  |  | 11.2
[9 empty] | 1050-1489 |  |  | 15.9
[9 empty] | 1490-2600 |  |  | 25.6
|  | Bulb Type (Decorative) | 3-way |  |  |  | =>90 | Lumen Range | 250-449 |  |  | 5
[9 empty] | 450-799 |  |  | 8.9
[9 empty] | 800-1099 |  |  | 13.6
[9 empty] | 1100-1599 |  |  | 19.3
[9 empty] | 1600-1999 |  |  | 25.7
[9 empty] | 2000-2549 |  |  | 32.5
[9 empty] | 2550-2999 |  |  | 39.6
|  |  | Globe (medium and intermediate bases less than 750 lumens) | [5 empty] | 90-179 |  |  | 2.1
[9 empty] | 180-249 |  |  | 3.3
[9 empty] | 250-349 |  |  | 4.6
[9 empty] | 350-749 |  |  | 8.5
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | [5 empty] | 70-89 |  |  | 1.2
[9 empty] | 90-149 |  |  | 1.8
[9 empty] | 150-299 |  |  | 3.5
[9 empty] | 300-749 |  |  | 8.1
|  |  | Globe (candelabra bases less than 750 lumens) | [5 empty] | 90-179 |  |  | 2.1
[9 empty] | 180-249 |  |  | 3.3
[9 empty] | 250-349 |  |  | 4.6
[9 empty] | 350-499 |  |  | 6.5
[9 empty] | 500-1049 |  |  | 11.9
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra 1050 lumens) | [5 empty] | 70-89 |  |  | 1.2
[9 empty] | 90-149 |  |  | 1.8
[9 empty] | 150-299 |  |  | 3.5
[9 empty] | 300-499 |  |  | 6.1
[9 empty] | 500-1049 |  |  | 11.9
|  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) | [5 empty] | 420-472 |  |  | 7.3
[9 empty] | 473-524 |  |  | 8.2
[9 empty] | 525-714 |  |  | 10.2
[9 empty] | 715-937 |  |  | 13.5
[9 empty] | 938-1259 |  |  | 18
[9 empty] | 1260-1399 |  |  | 21.8
[9 empty] | 1400-1739 |  |  | 25.7
[9 empty] | 1740-2174 |  |  | 32.1
[9 empty] | 2175-2624 |  |  | 39.3
[9 empty] | 2625-2999 |  |  | 46.1
[9 empty] | 3000-4500 |  |  | 61.5
|  |  | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" | [5 empty] | 400-449 |  |  | 7
[9 empty] | 450-499 |  |  | 7.8
[9 empty] | 500-649 |  |  | 9.4
[9 empty] | 650-1199 |  |  | 15.2
|  |  | *ER30, BR30, BR40, or ER40 | [5 empty] | 400-449 |  |  | 7
[9 empty] | 450-499 |  |  | 7.8
[9 empty] | 500-649 |  |  | 9.4
|  |  | BR30, BR40, or ER 40 | [5 empty] | 650-1419 |  |  | 17
|  |  | R20 | [5 empty] | 400-449 |  |  | 7
[9 empty] | 450-719 |  |  | 9.6
|  |  | *All reflector lamps below lumen ranges specified above | [5 empty] | 200-299 |  |  | 4.1
[9 empty] | 300-399 |  |  | 5.7
|  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) | [5 empty] | 250-309 |  |  | 4
[9 empty] | 310-749 |  |  | 7.6
[9 empty] | 750-1049 |  |  | 12.9
[9 empty] | 1050-1489 |  |  | 18.1
[9 empty] | 1490-2600 |  |  | 29.2
|  | Bulb Type (Decorative) | 3-way |  | CEE Tier 2 |  | <90 | Lumen Range | 250-449 |  |  | 3.7
[9 empty] | 450-799 |  |  | 6.6
[9 empty] | 800-1099 |  |  | 10
[9 empty] | 1100-1599 |  |  | 14.2
[9 empty] | 1600-1999 |  |  | 18.9
[9 empty] | 2000-2549 |  |  | 23.9
[9 empty] | 2550-2999 |  |  | 29.2
|  |  | Globe (medium and intermediate bases less than 750 lumens) | [5 empty] | 90-179 |  |  | 1.4
[9 empty] | 180-249 |  |  | 2.3
[9 empty] | 250-349 |  |  | 3.2
[9 empty] | 350-749 |  |  | 5.8
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | [5 empty] | 70-89 |  |  | 0.8
[9 empty] | 90-149 |  |  | 1.3
[9 empty] | 150-299 |  |  | 2.4
[9 empty] | 300-749 |  |  | 5.5
|  |  | Globe (candelabra bases less than 750 lumens) | [5 empty] | 90-179 |  |  | 1.4
[9 empty] | 180-249 |  |  | 2.3
[9 empty] | 250-349 |  |  | 3.2
[9 empty] | 350-499 |  |  | 4.5
[9 empty] | 500-1049 |  |  | 8.2
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra 1050 lumens) | [5 empty] | 70-89 |  |  | 0.8
[9 empty] | 90-149 |  |  | 1.3
[9 empty] | 150-299 |  |  | 2.4
[9 empty] | 300-499 |  |  | 4.2
[9 empty] | 500-1049 |  |  | 8.2
|  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) | [5 empty] | 420-472 |  |  | 5.2
[9 empty] | 473-524 |  |  | 5.9
[9 empty] | 525-714 |  |  | 7.3
[9 empty] | 715-937 |  |  | 9.7
[9 empty] | 938-1259 |  |  | 12.9
[9 empty] | 1260-1399 |  |  | 15.6
[9 empty] | 1400-1739 |  |  | 18.5
[9 empty] | 1740-2174 |  |  | 23
[9 empty] | 2175-2624 |  |  | 28.2
[9 empty] | 2625-2999 |  |  | 33.1
[9 empty] | 3000-4500 |  |  | 44.1
|  |  | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" | [5 empty] | 400-449 |  |  | 5
[9 empty] | 450-499 |  |  | 5.6
[9 empty] | 500-649 |  |  | 6.8
[9 empty] | 650-1199 |  |  | 10.9
|  |  | *ER30, BR30, BR40, or ER40 | [5 empty] | 400-449 |  |  | 5
[9 empty] | 450-499 |  |  | 5.6
[9 empty] | 500-649 |  |  | 6.8
|  |  | BR30, BR40, or ER 40 | [5 empty] | 650-1419 |  |  | 12.2
|  |  | R20 | [5 empty] | 400-449 |  |  | 5
[9 empty] | 450-719 |  |  | 6.9
|  |  | *All reflector lamps below lumen ranges specified above | [5 empty] | 200-299 |  |  | 2.9
[9 empty] | 300-399 |  |  | 4.1
|  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) | [5 empty] | 250-309 |  |  | 2.9
[9 empty] | 310-749 |  |  | 5.6
[9 empty] | 750-1049 |  |  | 9.5
[9 empty] | 1050-1489 |  |  | 13.4
[9 empty] | 1490-2600 |  |  | 21.5
|  | Bulb Type (Decorative) | 3-way |  |  |  | =>90 | Lumen Range | 250-449 |  |  | 4.4
[9 empty] | 450-799 |  |  | 7.8
[9 empty] | 800-1099 |  |  | 11.9
[9 empty] | 1100-1599 |  |  | 16.9
[9 empty] | 1600-1999 |  |  | 22.5
[9 empty] | 2000-2549 |  |  | 28.4
[9 empty] | 2550-2999 |  |  | 34.7
|  |  | Globe (medium and intermediate bases less than 750 lumens) | [5 empty] | 90-179 |  |  | 1.7
[9 empty] | 180-249 |  |  | 2.7
[9 empty] | 250-349 |  |  | 3.7
[9 empty] | 350-749 |  |  | 6.9
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | [5 empty] | 70-89 |  |  | 1
[9 empty] | 90-149 |  |  | 1.5
[9 empty] | 150-299 |  |  | 2.8
[9 empty] | 300-749 |  |  | 6.6
|  |  | Globe (candelabra bases less than 750 lumens) | [5 empty] | 90-179 |  |  | 1.7
[9 empty] | 180-249 |  |  | 2.7
[9 empty] | 250-349 |  |  | 3.7
[9 empty] | 350-499 |  |  | 5.3
[9 empty] | 500-1049 |  |  | 9.7
|  |  | Decorative (Shapes B, BA, C, CA, DC, F, G, candelabra 1050 lumens) | [5 empty] | 70-89 |  |  | 1
[9 empty] | 90-149 |  |  | 1.5
[9 empty] | 150-299 |  |  | 2.8
[9 empty] | 300-499 |  |  | 5
[9 empty] | 500-1049 |  |  | 9.7
|  | Bulb Type (Directional) | R, ER, BR with medium screw bases w/ diameter >2.25" (*see exceptions below) | [5 empty] | 420-472 |  |  | 6.4
[9 empty] | 473-524 |  |  | 7.1
[9 empty] | 525-714 |  |  | 8.9
[9 empty] | 715-937 |  |  | 11.8
[9 empty] | 938-1259 |  |  | 15.7
[9 empty] | 1260-1399 |  |  | 19
[9 empty] | 1400-1739 |  |  | 22.4
[9 empty] | 1740-2174 |  |  | 28
[9 empty] | 2175-2624 |  |  | 34.3
[9 empty] | 2625-2999 |  |  | 40.2
[9 empty] | 3000-4500 |  |  | 53.6
|  |  | *R, BR, and ER with medium screw bases w/ diameter ≤2.25" | [5 empty] | 400-449 |  |  | 6.1
[9 empty] | 450-499 |  |  | 6.8
[9 empty] | 500-649 |  |  | 8.2
[9 empty] | 650-1199 |  |  | 13.2
|  |  | *ER30, BR30, BR40, or ER40 | [5 empty] | 400-449 |  |  | 6.1
[9 empty] | 450-499 |  |  | 6.8
[9 empty] | 500-649 |  |  | 8.2
|  |  | BR30, BR40, or ER 40 | [5 empty] | 650-1419 |  |  | 14.8
|  |  | R20 | [5 empty] | 400-449 |  |  | 6.1
[9 empty] | 450-719 |  |  | 8.4
|  |  | *All reflector lamps below lumen ranges specified above | [5 empty] | 200-299 |  |  | 3.6
[9 empty] | 300-399 |  |  | 5
|  | Bulb Type (EISA non-exempt bulb types) | Dimmable Twist, Globe (less than 5" in diameter and > 749 lumens), candle (shapes B, BA, CA > 749 lumens), Candelabra Base Lamps (>1049 lumens), Intermediate Base Lamps (>749 lumens) | [5 empty] | 250-309 |  |  | 3.5
[9 empty] | 310-749 |  |  | 6.6
[9 empty] | 750-1049 |  |  | 11.2
[9 empty] | 1050-1489 |  |  | 15.9
[9 empty] | 1490-2600 |  |  | 25.6
| [Hours] | Building Type | Agricultural Animal Housing and Warehousing | [8 empty] | 2920 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Convenience | [8 empty] | 4630
|  |  | Education | [8 empty] | 1877
|  |  | Exterior Lighting | [8 empty] | 4676
|  |  | Grocery | [8 empty] | 4663
|  |  | Health | [8 empty] | 3806
|  |  | Hospital | [8 empty] | 6520
|  |  | Industrial | [8 empty] | 2850
|  |  | Lodging | [8 empty] | 3061
|  |  | Multifamily | [8 empty] | 3061
|  |  | Office - Large | [8 empty] | 2920
|  |  | Office - Small | [8 empty] | 2920
|  |  | Religious | [8 empty] | 2412
|  |  | Restaurant | [8 empty] | 5443
|  |  | Retail - Large | [8 empty] | 4065
|  |  | Retail - Small | [8 empty] | 3694
|  |  | Warehouse | [8 empty] | 2920
|  |  | Nonresidential Average | [8 empty] | 3065
|  |  | Unconditioned building | [8 empty] | As specific building above
|  |  | Refrigerated Cases | [8 empty] | As specific building above
|  |  | Freezer Cases | [8 empty] | As specific building above
| [WHFe] | Building Type | Agricultural Animal Housing and Warehousing | [8 empty] | 1 | N |  | Waste heat factors for energy to account for cooling energy savings from efficient lighting
|  |  | Convenience | [8 empty] | 1.14
|  |  | Education | [8 empty] | 1.07
|  |  | Exterior Lighting | [8 empty] | 1
|  |  | Grocery | [8 empty] | 1.02
|  |  | Health | [8 empty] | 1.09
|  |  | Hospital | [8 empty] | 1.16
|  |  | Industrial | [8 empty] | 1.02
|  |  | Lodging | [8 empty] | 1.23
|  |  | Multifamily | [8 empty] | 1.13
|  |  | Office - Large | [8 empty] | 1.17
|  |  | Office - Small | [8 empty] | 1.1
|  |  | Religious | [8 empty] | 1.12
|  |  | Restaurant | [8 empty] | 1
|  |  | Retail - Large | [8 empty] | 1
|  |  | Retail - Small | [8 empty] | 1.09
|  |  | Warehouse | [8 empty] | 1
|  |  | Nonresidential Average | [8 empty] | 1.06
|  |  | Unconditioned building | [8 empty] | 1
|  |  | Refrigerated Cases | [8 empty] | 1.29
|  |  | Freezer Cases | [8 empty] | 1.5
| [ISR] | Program | Retail (Time of Sale) | [8 empty] | 89% | Y |  | In Service Rate or the percentage of units that get installed
|  |  | Direct Install and Retrofit | [8 empty] | 97%
| [MidLifeAdj] | Year | Pre 2025 | [8 empty] | 100%
|  |  | 2025 on | Lamp Category | Decorative and Globe | Efficiency Level | ENERGY STAR |  |  |  |  | 57% | N | Percentage | Mid Life Adjustment to account for baseline shifting within the measure life to a CFL in 2020. This factor should be applied to the annual savings for years 2021 onwards for any measure installed prior to 2021.
[7 empty] | CEE Tier 2 |  |  |  |  | 63%
[5 empty] | Directional |  | ENERGY STAR |  |  |  |  | 62%
[7 empty] | CEE Tier 2 |  |  |  |  | 69%
| [ΔkWhheatpenalty] | [11 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Agricultural Animal Housing and Warehousing | Heating Type | Resistance | [6 empty] | 0 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Convenience | [8 empty] | 0.36
|  |  | Education | [8 empty] | 0.45
|  |  | Exterior Lighting | [8 empty] | 0
|  |  | Grocery | [8 empty] | 0.3
|  |  | Health | [8 empty] | 0.35
|  |  | Hospital | [8 empty] | 0.18
|  |  | Industrial | [8 empty] | 0.37
|  |  | Lodging | [8 empty] | 0.19
|  |  | Multifamily | [8 empty] | 0.44
|  |  | Office - Large | [8 empty] | 0.29
|  |  | Office - Small | [8 empty] | 0.33
|  |  | Religious | [8 empty] | 0.46
|  |  | Restaurant | [8 empty] | 0
|  |  | Retail - Large | [8 empty] | 0
|  |  | Retail - Small | [8 empty] | 0.36
|  |  | Warehouse | [8 empty] | 0
|  |  | Nonresidential Average | [8 empty] | 0.24
|  |  | Unconditioned building | [8 empty] | 0
|  |  | Refrigerated Cases | [8 empty] | 0
|  |  | Freezer Cases | [8 empty] | 0
|  |  | Agricultural Animal Housing and Warehousing |  | Heat Pump | [6 empty] | 0
|  |  | Convenience | [8 empty] | 0.16
|  |  | Education | [8 empty] | 0.2
|  |  | Exterior Lighting | [8 empty] | 0
|  |  | Grocery | [8 empty] | 0.13
|  |  | Health | [8 empty] | 0.15
|  |  | Hospital | [8 empty] | 0.08
|  |  | Industrial | [8 empty] | 0.16
|  |  | Lodging | [8 empty] | 0.08
|  |  | Multifamily | [8 empty] | 0.19
|  |  | Office - Large | [8 empty] | 0.13
|  |  | Office - Small | [8 empty] | 0.15
|  |  | Religious | [8 empty] | 0.2
|  |  | Restaurant | [8 empty] | 0
|  |  | Retail - Large | [8 empty] | 0
|  |  | Retail - Small | [8 empty] | 0.16
|  |  | Warehouse | [8 empty] | 0
|  |  | Nonresidential Average | [8 empty] | 0.1
|  |  | Unconditioned building | [8 empty] | 0
|  |  | Refrigerated Cases | [8 empty] | 0
|  |  | Freezer Cases | [8 empty] | 0
| [WHFd] | Building Type | Agricultural Animal Housing and Warehousing | [8 empty] | 1 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Convenience | [8 empty] | 1.31
|  |  | Education | [8 empty] | 1.48
|  |  | Exterior Lighting | [8 empty] | 1
|  |  | Grocery | [8 empty] | 1.2
|  |  | Health | [8 empty] | 1.69
|  |  | Hospital | [8 empty] | 1.26
|  |  | Industrial | [8 empty] | 1.02
|  |  | Lodging | [8 empty] | 1.47
|  |  | Multifamily | [8 empty] | 1.15
|  |  | Office - Large | [8 empty] | 1.04
|  |  | Office - Small | [8 empty] | 1.28
|  |  | Religious | [8 empty] | 1.32
|  |  | Restaurant | [8 empty] | 1.47
|  |  | Retail - Large | [8 empty] | 1.28
|  |  | Retail - Small | [8 empty] | 1.2
|  |  | Warehouse | [8 empty] | 1.19
|  |  | Nonresidential Average | [8 empty] | 1.28
|  |  | Unconditioned building | [8 empty] | 1
|  |  | Refrigerated Cases | [8 empty] | 1.29
|  |  | Freezer Cases | [8 empty] | 1.5
| [CF] | Building Type | Agricultural Animal Housing and Warehousing | [8 empty] | 61.8% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Convenience | [8 empty] | 100%
|  |  | Education | [8 empty] | 65.27%
|  |  | Exterior Lighting | [8 empty] | 0%
|  |  | Grocery | [8 empty] | 82.11%
|  |  | Health | [8 empty] | 67%
|  |  | Hospital | [8 empty] | 55.95%
|  |  | Industrial | [8 empty] | 91.8%
|  |  | Lodging | [8 empty] | 61.07%
|  |  | Multifamily | [8 empty] | 71.17%
|  |  | Office - Large | [8 empty] | 60.2%
|  |  | Office - Small | [8 empty] | 51.79%
|  |  | Religious | [8 empty] | 66%
|  |  | Restaurant | [8 empty] | 100%
|  |  | Retail - Large | [8 empty] | 100%
|  |  | Retail - Small | [8 empty] | 100%
|  |  | Warehouse | [8 empty] | 61.8%
|  |  | Nonresidential Average | [8 empty] | 69.07%
|  |  | Unconditioned building | [8 empty] | As specific building above
|  |  | Refrigerated Cases | [8 empty] | As specific building above
|  |  | Freezer Cases | [8 empty] | As specific building above
| [IFTherms] | Building Type | Agricultural Animal Housing and Warehousing | [8 empty] | 0 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Convenience | [8 empty] | 0.015
|  |  | Education | [8 empty] | 0.019
|  |  | Exterior Lighting | [8 empty] | 0
|  |  | Grocery | [8 empty] | 0.013
|  |  | Health | [8 empty] | 0.015
|  |  | Hospital | [8 empty] | 0.008
|  |  | Industrial | [8 empty] | 0.016
|  |  | Lodging | [8 empty] | 0.008
|  |  | Multifamily | [8 empty] | 0.019
|  |  | Office - Large | [8 empty] | 0.013
|  |  | Office - Small | [8 empty] | 0.014
|  |  | Religious | [8 empty] | 0.02
|  |  | Restaurant | [8 empty] | 0
|  |  | Retail - Large | [8 empty] | 0
|  |  | Retail - Small | [8 empty] | 0.015
|  |  | Warehouse | [8 empty] | 0
|  |  | Nonresidential Average | [8 empty] | 0.01
|  |  | Unconditioned building | [8 empty] | 0
|  |  | Refrigerated Cases | [8 empty] | 0
|  |  | Freezer Cases | [8 empty] | 0
| [ΔTherms] | [11 empty] | C | Therms | Therm impact calculated above
| [HeatDays] | [10 empty] | 197 | N | Days | Heat season days per year

## LED Fixtures
LED Fixtures
| Measure Code: | NR-LTG-LDFX-V04-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
13
| Measure Cost: | Please see reference tables in 3.4.5 |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| O&M Cost: | Please see reference tables in 3.4.5
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([WattsBase] - [WattsEE]) / [1,000] * [Hours] * [WHFe] * [ISR] * [MidLifeAdj]
| Time of Sale Demand (ΔkW) | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [WHFd] * [CF] * [MidLifeAdj]
| Time of Sale Gas (ΔTherms) | = ([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] *(- [IFTherms]) * [MidLifeAdj]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] * (-[IFkWh])
| [MidLifeAdj] |  |  | =(([WattsT8base] -[WattsEE])/([WattsBase] - [WattsEE]))
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Category | LED Downlight Fixtures | Description | 40% CFL 26W Pin Based & 60% PAR30/38 | 54.3 | N | Watts | Input wattage of the existing or baseline system.
|  |  | LED Interior Directional |  | 10% CMH PAR38 & 90% Halogen PAR38 | 60.4
[5 empty] | 40% CFL 42W Pin Base & 60% Halogen PAR38 | 17.7
|  |  | LED Display Case |  | 50% 2’T5 Linear & 50% 50W Halogen | 36.2/ft
[5 empty] | 50% 2’T5 Linear & 50% 50W Halogen | 36.2/ft
[5 empty] | 5’T8 | 15.2/ft
[5 empty] | 6’T12HO | 18.7/ft
|  |  | LED Linear Replacement Lamps |  | F17T8 Standard Lamp - 2 foot | 15
[5 empty] | F32T8 Standard Lamp - 4 foot | 28.2
[5 empty] | F32T8/HO Standard Lamp - 4 foot | 4.2
|  |  | LED Troffers |  | 18:82; 2-Lamp 34w T12 (BF < 0.85) :2-Lamp 32w T8 (BF < 0.89) | 57.9
[5 empty] | 18:82; 3-Lamp 34w T12 (BF <0.88) :3-Lamp 32w T8 (BF < 0.88) | 88.7
[5 empty] | 18:82; 2-Lamp 34w T12 (BF < 0.85) :2-Lamp 32w T8 (BF < 0.89) | 57.9
[5 empty] | 18:82; 3-Lamp 34w T12 (BF <0.88) :3-Lamp 32w T8 (BF < 0.88) | 88.7
[5 empty] | 18:82;4-Lamp 34w T12 (BF < 0.88): 4-Lamp 32w T8 (BF < 0.88) | 118.3
[5 empty] | 18:82; 1-Lamp 34w T12 (BF <0.88) : 1-Lamp 32w T8 (BF <0.91) | 29.5
[5 empty] | 18:82; 2-Lamp 34w T12 (BF < 0.85) :2-Lamp 32w T8 (BF < 0.89) | 57.9
[5 empty] | 18:82; 3-Lamp 34w T12 (BF <0.88) :3-Lamp 32w T8 (BF < 0.88) | 88.7
|  |  | LED Linear Ambiant Fixtures |  | 18:82; 1-Lamp 34w T12 (BF <0.88) : 1-Lamp 32w T8 (BF <0.91) | 29.5
[5 empty] | 18:82; 2-Lamp 34w T12 (BF < 0.85) :2-Lamp 32w T8 (BF < 0.89) | 57.9
[5 empty] | 18:82; 3-Lamp 34w T12 (BF <0.88) :3-Lamp 32w T8 (BF < 0.88) | 88.7
[5 empty] | T5HO 2L-F54T5HO - 4' | 120
[5 empty] | T5HO 3L-F54T5HO - 4' | 180
|  |  | LED High & Low Bay Fixtures |  | 3-Lamp T8HO Low-Bay | 157
[5 empty] | 4-Lamp T8HO High-Bay | 196
[5 empty] | 6-Lamp T8HO High-Bay | 294
[5 empty] | 8-Lamp T8HO High-Bay | 392
|  |  | LED Agricultural Interior Fixtures |  | 25% 73 Watt EISA Inc, 75% 1L T8 | 42
[5 empty] | 25% 146 Watt EISA Inc, 75% 2L T8 | 81
[5 empty] | 25% 217 Watt EISA Inc, 75% 3L T8 | 121
[5 empty] | 25% 292 Watt EISA Inc, 75% 4L T8 | 159
[5 empty] | 200W Pulse Start Metal Halide | 227.3
[5 empty] | 320W Pulse Start Metal Halide | 363.6
[5 empty] | 350W Pulse Start Metal Halide | 397.7
[5 empty] | (2) 320W Pulse Start Metal Halide | 727.3
|  |  | LED Exterior Fictures |  | 100W Metal Halide | 113.6
[5 empty] | 175W Pulse Start Metal Halide | 198.9
[5 empty] | 250W Pulse Start Metal Halide | 284.1
[5 empty] | 400W Pulse Start Metal Halide | 454.5
| [WattsEE] | Category | LED Downlight Fixtures | Description | LED Recessed, Surface, Pendant Downlights | 17.6 | N | Watts | Actual wattage of LED fixture purchased / installed. If unknown, use default provided in
|  |  | LED Interior Directional |  | LED Track Lighting | 12.2
[5 empty] | LED Wall-Wash Fixtures | 8.3
|  |  | LED Display Case |  | LED Display Case Light Fixture | 7.1
[5 empty] | LED Undercabinet Shelf-Mounted Task Light Fixtures | 7.1
[5 empty] | LED Refrigerated Case Light, Horizontal or Vertical | 7.6
[5 empty] | LED Freezer Case Light, Horizontal or Vertical | 7.6667
|  |  | LED Linear Replacement Lamps |  | T8 LED Replacement Lamp (TLED), < 1200 lumens | 8.9
[5 empty] | T8 LED Replacement Lamp (TLED), 1200-2400 lumens | 15.8
[5 empty] | T8 LED Replacement Lamp (TLED), 2401-4000 lumens | 22.9
|  |  | LED Troffers |  | LED 2x2 Recessed Light Fixture, 2000-3500 lumens | 25.4
[5 empty] | LED 2x2 Recessed Light Fixture, 3501-5000 lumens | 36.7
[5 empty] | LED 2x4 Recessed Light Fixture, 3000-4500 lumens | 33.3
[5 empty] | LED 2x4 Recessed Light Fixture, 4501-6000 lumens | 44.8
[5 empty] | LED 2x4 Recessed Light Fixture, 6001-7500 lumens | 57.2
[5 empty] | LED 1x4 Recessed Light Fixture, 1500-3000 lumens | 21.8
[5 empty] | LED 1x4 Recessed Light Fixture, 3001-4500 lumens | 33.7
[5 empty] | LED 1x4 Recessed Light Fixture, 4501-6000 lumens | 43.3
|  |  | LED Linear Ambiant Fixtures |  | LED Surface & Suspended Linear Fixture, <= 3000 lumens | 19.5
[5 empty] | LED Surface & Suspended Linear Fixture, 3001-4500 lumens | 32.1
[5 empty] | LED Surface & Suspended Linear Fixture, 4501-6000 lumens | 43.5
[5 empty] | LED Surface & Suspended Linear Fixture, 6001-7500 lumens | 56.3
[5 empty] | LED Surface & Suspended Linear Fixture, > 7500 lumens | 82.4
|  |  | LED High & Low Bay Fixtures |  | LED Low-Bay Fixtures, <= 10,000 lumens | 61.6
[5 empty] | LED High-Bay Fixtures, 10,001-15,000 lumens | 99.5
[5 empty] | LED High-Bay Fixtures, 15,001-20,000 lumens | 140.2
[5 empty] | LED High-Bay Fixtures, => 20,000 lumens | 193.8
|  |  | LED Agricultural Interior Fixtures |  | LED Ag Interior Fixtures, <= 2,000 lumens | 12.9
[5 empty] | LED Ag Interior Fixtures, 2,001-4,000 lumens | 29.7
[5 empty] | LED Ag Interior Fixtures, 4,001-6,000 lumens | 45.1
[5 empty] | LED Ag Interior Fixtures, 6,001-8,000 lumens | 59.7
[5 empty] | LED Ag Interior Fixtures, 8,001-12,000 lumens | 84.9
[5 empty] | LED Ag Interior Fixtures, 12,001-16,000 lumens | 113.9
[5 empty] | LED Ag Interior Fixtures, 16,001-20,000 lumens | 143.7
[5 empty] | LED Ag Interior Fixtures, => 20,000 lumens | 193.8
|  |  | LED Exterior Fictures |  | LED Exterior Fixtures, <= 5,000 lumens | 34.1
[5 empty] | LED Exterior Fixtures, 5,001-10,000 lumens | 67.2
[5 empty] | LED Exterior Fixtures, 10,001-15,000 lumens | 108.8
[5 empty] | LED Exterior Fixtures, => 15,000 lumens | 183.9
| [Hours] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 2920 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Convenience |  |  | 4630
|  |  | Education |  |  | 1877
|  |  | Exterior Lighting |  |  | 4676
|  |  | Grocery |  |  | 4663
|  |  | Health |  |  | 3806
|  |  | Hospital |  |  | 6520
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3061
|  |  | Multifamily |  |  | 3061
|  |  | Office - Large |  |  | 2920
|  |  | Office - Small |  |  | 2920
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 5443
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 3694
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 3065
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [WHFe] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 1 | N | Hours | Waste heat factors for energy to account for cooling energy savings from efficient lighting
|  |  | Convenience |  |  | 1.14
|  |  | Education |  |  | 1.07
|  |  | Exterior Lighting |  |  | 1
|  |  | Grocery |  |  | 1.02
|  |  | Health |  |  | 1.09
|  |  | Hospital |  |  | 1.16
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.23
|  |  | Multifamily |  |  | 1.13
|  |  | Office - Large |  |  | 1.17
|  |  | Office - Small |  |  | 1.1
|  |  | Religious |  |  | 1.12
|  |  | Restaurant |  |  | 1
|  |  | Retail - Large |  |  | 1
|  |  | Retail - Small |  |  | 1.09
|  |  | Warehouse |  |  | 1
|  |  | Nonresidential Average |  |  | 1.06
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [ISR] | Program Type | Time of Sale |  |  | 95% | N |  | In Servce Rate or the percentage of units rebated that get installed
|  |  | Retrofit |  |  | 100%
| [ΔkWhheatpenalty] | [5 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Agricultural Animal Housing and Warehousing | Heating Type | Resistance | 0 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Convenience |  |  | 0.36
|  |  | Education |  |  | 0.45
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.3
|  |  | Health |  |  | 0.35
|  |  | Hospital |  |  | 0.18
|  |  | Industrial |  |  | 0.37
|  |  | Lodging |  |  | 0.19
|  |  | Multifamily |  |  | 0.44
|  |  | Office - Large |  |  | 0.29
|  |  | Office - Small |  |  | 0.33
|  |  | Religious |  |  | 0.46
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.36
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.24
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
|  |  | Agricultural Animal Housing and Warehousing |  | Heat Pump | 0
|  |  | Convenience |  |  | 0.16
|  |  | Education |  |  | 0.2
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.13
|  |  | Health |  |  | 0.15
|  |  | Hospital |  |  | 0.08
|  |  | Industrial |  |  | 0.16
|  |  | Lodging |  |  | 0.08
|  |  | Multifamily |  |  | 0.19
|  |  | Office - Large |  |  | 0.13
|  |  | Office - Small |  |  | 0.15
|  |  | Religious |  |  | 0.2
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.16
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.1
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [MidLifeAdj] | [5 empty] | C |  | A midlife savings adjustment should be applied to any measure with a blended T12:Standard T8 baseline. The adjustment should occur in 2020 to account for the baseline lamp replacement assumption changing from a blended 82/18 Standard T8/T12 to 100% Standard T8 by 2020.
| [WattsT8Base] | Category | LED Linear Replacement Lamps | Description | LED 4' Linear Replacement Lamp | 32 | N | Watts | Input wattage of the existing system based on 100% T8 fixture
[5 empty] | LED 2' Linear Replacement Lamp | 17
|  |  | LED Troffers |  | LED 2x2 Recessed Light Fixture, 2000-3500 lumens | 56.96
[5 empty] | LED 2x2 Recessed Light Fixture, 3501-5000 lumens | 84.48
[5 empty] | LED 2x4 Recessed Light Fixture, 3000-4500 lumens | 56.96
[5 empty] | LED 2x4 Recessed Light Fixture, 4501-6000 lumens | 84.48
[5 empty] | LED 2x4 Recessed Light Fixture, 6001-7500 lumens | 113
[5 empty] | LED 1x4 Recessed Light Fixture, 1500-3000 lumens | 29.12
[5 empty] | LED 1x4 Recessed Light Fixture, 3001-4500 lumens | 56.96
[5 empty] | LED 1x4 Recessed Light Fixture, 4501-6000 lumens | 84.48
|  |  | LED Linear Ambient Fixtures |  | LED Surface & Suspended Linear Fixture, ≤ 3000 lumens | 29.12
[5 empty] | LED Surface & Suspended Linear Fixture, 3001-4500 lumens | 56.96
[5 empty] | LED Surface & Suspended Linear Fixture, 4501-6000 lumens | 84.48
| [WHFd] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 1 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Convenience |  |  | 1.31
|  |  | Education |  |  | 1.48
|  |  | Exterior Lighting |  |  | 1
|  |  | Grocery |  |  | 1.2
|  |  | Health |  |  | 1.69
|  |  | Hospital |  |  | 1.26
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.47
|  |  | Multifamily |  |  | 1.15
|  |  | Office - Large |  |  | 1.04
|  |  | Office - Small |  |  | 1.28
|  |  | Religious |  |  | 1.32
|  |  | Restaurant |  |  | 1.47
|  |  | Retail - Large |  |  | 1.28
|  |  | Retail - Small |  |  | 1.2
|  |  | Warehouse |  |  | 1.19
|  |  | Nonresidential Average |  |  | 1.28
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [CF] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 61.8% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Convenience |  |  | 100%
|  |  | Education |  |  | 65.27%
|  |  | Exterior Lighting |  |  | 0%
|  |  | Grocery |  |  | 82.11%
|  |  | Health |  |  | 67%
|  |  | Hospital |  |  | 55.95%
|  |  | Industrial |  |  | 91.8%
|  |  | Lodging |  |  | 61.07%
|  |  | Multifamily |  |  | 71.17%
|  |  | Office - Large |  |  | 60.2%
|  |  | Office - Small |  |  | 51.79%
|  |  | Religious |  |  | 66%
|  |  | Restaurant |  |  | 100%
|  |  | Retail - Large |  |  | 100%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 61.8%
|  |  | Nonresidential Average |  |  | 69.07%
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [IFTherms] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 0 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Convenience |  |  | 0.015
|  |  | Education |  |  | 0.019
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.013
|  |  | Health |  |  | 0.015
|  |  | Hospital |  |  | 0.008
|  |  | Industrial |  |  | 0.016
|  |  | Lodging |  |  | 0.008
|  |  | Multifamily |  |  | 0.019
|  |  | Office - Large |  |  | 0.013
|  |  | Office - Small |  |  | 0.014
|  |  | Religious |  |  | 0.02
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.015
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.01
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [ΔTherms] | [5 empty] | C | Therms | Therm impact calculated above
| [HeatDays] |  |  |  |  | 197 | N | Days | Heat season days per year

## T5 HO Fix. and Lamp and Ballast
T5 HO Fix. and Lamp and Ballast
| Measure Code: | NR-LTG-T5HO-V02-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
100
| O&M Cost: | Please see reference tables in 3.4.6
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([WattsBase] - [WattsEE]) / [1,000] * [Hours] * [WHFe] * [ISR]
| Time of Sale Demand (ΔkW) | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [WHFd] * [CF]
| Time of Sale Gas (ΔTherms) | = ([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] *(- [IFTherms])
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Lamp Type | 3-Lamp T5 High-Bay | Baseline Description | 200 Watt Pulse Start Metal-Halide | 227 | Y | Watts | Actual (if retrofit) or based on lumens of CFL bulb installed
|  |  | 4-Lamp T5 High-Bay |  | 320 Watt Pulse Start Metal-Halide | 364
|  |  | 6-Lamp T5 High-Bay |  | 400 Watt Pulse Start Metal-Halide | 455
|  |  | 8-Lamp T5 High-Bay |  | 750 Watt Pulse Start Metal-Halide | 825
| [WattsEE] | Lamp Type | 3-Lamp T5 High-Bay |  |  | 176 | Y | Watts | Actual wattage of CFL purchased or installed
|  |  | 4-Lamp T5 High-Bay |  |  | 235
|  |  | 6-Lamp T5 High-Bay |  |  | 352
|  |  | 8-Lamp T5 High-Bay |  |  | 470
| [Hours] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 2920 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Convenience |  |  | 4630
|  |  | Education |  |  | 1877
|  |  | Exterior Lighting |  |  | 4676
|  |  | Grocery |  |  | 4663
|  |  | Health |  |  | 3806
|  |  | Hospital |  |  | 6520
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3061
|  |  | Multifamily |  |  | 3061
|  |  | Office - Large |  |  | 2920
|  |  | Office - Small |  |  | 2920
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 5443
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 3694
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 3065
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [WHFe] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 1 | N | Hours | Waste heat factors for energy to account for cooling energy savings from efficient lighting
|  |  | Convenience |  |  | 1.14
|  |  | Education |  |  | 1.07
|  |  | Exterior Lighting |  |  | 1
|  |  | Grocery |  |  | 1.02
|  |  | Health |  |  | 1.09
|  |  | Hospital |  |  | 1.16
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.23
|  |  | Multifamily |  |  | 1.13
|  |  | Office - Large |  |  | 1.17
|  |  | Office - Small |  |  | 1.1
|  |  | Religious |  |  | 1.12
|  |  | Restaurant |  |  | 1
|  |  | Retail - Large |  |  | 1
|  |  | Retail - Small |  |  | 1.09
|  |  | Warehouse |  |  | 1
|  |  | Nonresidential Average |  |  | 1.06
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [ISR] | Form completed? | Yes |  |  | 100% | N |  | In Servce Rate or the percentage of units rebated that get installed
|  |  | No |  |  | 98%
| [ΔkWhheatpenalty] | [5 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Agricultural Animal Housing and Warehousing | Heating Type | Resistance | 0 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Convenience |  |  | 0.36
|  |  | Education |  |  | 0.45
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.3
|  |  | Health |  |  | 0.35
|  |  | Hospital |  |  | 0.18
|  |  | Industrial |  |  | 0.37
|  |  | Lodging |  |  | 0.19
|  |  | Multifamily |  |  | 0.44
|  |  | Office - Large |  |  | 0.29
|  |  | Office - Small |  |  | 0.33
|  |  | Religious |  |  | 0.46
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.36
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.24
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
|  |  | Agricultural Animal Housing and Warehousing |  | Heat Pump | 0
|  |  | Convenience |  |  | 0.16
|  |  | Education |  |  | 0.2
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.13
|  |  | Health |  |  | 0.15
|  |  | Hospital |  |  | 0.08
|  |  | Industrial |  |  | 0.16
|  |  | Lodging |  |  | 0.08
|  |  | Multifamily |  |  | 0.19
|  |  | Office - Large |  |  | 0.13
|  |  | Office - Small |  |  | 0.15
|  |  | Religious |  |  | 0.2
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.16
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.1
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [WHFd] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 1 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Convenience |  |  | 1.31
|  |  | Education |  |  | 1.48
|  |  | Exterior Lighting |  |  | 1
|  |  | Grocery |  |  | 1.2
|  |  | Health |  |  | 1.69
|  |  | Hospital |  |  | 1.26
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.47
|  |  | Multifamily |  |  | 1.15
|  |  | Office - Large |  |  | 1.04
|  |  | Office - Small |  |  | 1.28
|  |  | Religious |  |  | 1.32
|  |  | Restaurant |  |  | 1.47
|  |  | Retail - Large |  |  | 1.28
|  |  | Retail - Small |  |  | 1.2
|  |  | Warehouse |  |  | 1.19
|  |  | Nonresidential Average |  |  | 1.28
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [CF] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 61.8% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Convenience |  |  | 100%
|  |  | Education |  |  | 65.27%
|  |  | Exterior Lighting |  |  | 0%
|  |  | Grocery |  |  | 82.11%
|  |  | Health |  |  | 67%
|  |  | Hospital |  |  | 55.95%
|  |  | Industrial |  |  | 91.8%
|  |  | Lodging |  |  | 61.07%
|  |  | Multifamily |  |  | 71.17%
|  |  | Office - Large |  |  | 60.2%
|  |  | Office - Small |  |  | 51.79%
|  |  | Religious |  |  | 66%
|  |  | Restaurant |  |  | 100%
|  |  | Retail - Large |  |  | 100%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 61.8%
|  |  | Nonresidential Average |  |  | 69.07%
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [IFTherms] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 0 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Convenience |  |  | 0.015
|  |  | Education |  |  | 0.019
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.013
|  |  | Health |  |  | 0.015
|  |  | Hospital |  |  | 0.008
|  |  | Industrial |  |  | 0.016
|  |  | Lodging |  |  | 0.008
|  |  | Multifamily |  |  | 0.019
|  |  | Office - Large |  |  | 0.013
|  |  | Office - Small |  |  | 0.014
|  |  | Religious |  |  | 0.02
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.015
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.01
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [ΔTherms] | [5 empty] | C | Therms | Therm impact calculated above
| [HeatDays] |  |  |  |  | 197 | N | Days | Heat season days per year

## HP and RW T8
HP and RW T8
| Measure Code: | NR-LTG-HPT8-V01-170101
Note: This measure is effective until 12/31/2017. It should not be used beyond that date but is left in the manual for reference purposes.
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Lamp Type | 1-Lamp 32w HPT8 (BF < 0.79) | 15
|  | 2-Lamp 32w HPT8 (BF < 0.77) | 17.5
|  | 3-Lamp 32w HPT8 (BF < 0.76) | 20
|  | 4-Lamp 32w HPT8 (BF < 0.78) | 22.5
|  | 6-Lamp 32w HPT8 (BF < 0.76) | 40
|  | 1-Lamp 28w RWT8 (BF < 0.76) | 15
|  | 2-Lamp 28w RWT8 (BF < 0.76) | 17.5
|  | 3-Lamp 28w RWT8 (BF < 0.77) | 20
|  | 4-Lamp 28w RWT8 (BF < 0.79) | 22.5
|  | 6-Lamp 28w RWT8 (BF < 0.77) | 40
| O&M Cost: | Please see reference tables in 3.4.7
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([WattsBase] - [WattsEE]) / [1,000] * [Hours] * [WHFe] * [ISR] * [MidLifeAdj]
| Time of Sale Demand (ΔkW) | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [WHFd] * [CF] * [MidLifeAdj]
| Time of Sale Gas (ΔTherms) | = ([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] *(- [IFTherms]) * [MidLifeAdj]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] * (-[IFkWh])
| [MidLifeAdj] |  |  | =(([WattsT8base] -[WattsEE])/([WattsBase] - [WattsEE]))
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Lamp Type | 1-Lamp 32w HPT8 (BF < 0.79) |  |  | 30.1 | N | Watts | Input wattage of the existing or baseline system.
|  |  | 2-Lamp 32w HPT8 (BF < 0.77) |  |  | 59.5
|  |  | 3-Lamp 32w HPT8 (BF < 0.76) |  |  | 96.2
|  |  | 4-Lamp 32w HPT8 (BF < 0.78) |  |  | 128.3
|  |  | 6-Lamp 32w HPT8 (BF < 0.76) |  |  | 192.5
|  |  | 1-Lamp 28w RWT8 (BF < 0.76) |  |  | 30.1
|  |  | 2-Lamp 28w RWT8 (BF < 0.76) |  |  | 59.5
|  |  | 3-Lamp 28w RWT8 (BF < 0.77) |  |  | 96.2
|  |  | 4-Lamp 28w RWT8 (BF < 0.79) |  |  | 128.3
|  |  | 6-Lamp 28w RWT8 (BF < 0.77) |  |  | 192.5
| [WattsEE] | Lamp Type | 1-Lamp 32w HPT8 (BF < 0.79) |  |  | 24 | N | Watts | Input wattage of the existing or baseline system.
|  |  | 2-Lamp 32w HPT8 (BF < 0.77) |  |  | 48
|  |  | 3-Lamp 32w HPT8 (BF < 0.76) |  |  | 71
|  |  | 4-Lamp 32w HPT8 (BF < 0.78) |  |  | 98
|  |  | 6-Lamp 32w HPT8 (BF < 0.76) |  |  | 142
|  |  | 1-Lamp 28w RWT8 (BF < 0.76) |  |  | 21
|  |  | 2-Lamp 28w RWT8 (BF < 0.76) |  |  | 43
|  |  | 3-Lamp 28w RWT8 (BF < 0.77) |  |  | 63
|  |  | 4-Lamp 28w RWT8 (BF < 0.79) |  |  | 88
|  |  | 6-Lamp 28w RWT8 (BF < 0.77) |  |  | 126
| [Hours] | Building Type | Convenience |  |  | 4630 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Education |  |  | 1877
|  |  | Grocery |  |  | 4663
|  |  | Health |  |  | 3806
|  |  | Hospital |  |  | 6520
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3061
|  |  | Multifamily |  |  | 3061
|  |  | Office - Large |  |  | 2920
|  |  | Office - Small |  |  | 2920
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 5443
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 3694
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 3065
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [WHFe] | Building Type | Convenience |  |  | 1.14 | N | Hours | Waste heat factors for energy to account for cooling energy savings from efficient lighting
|  |  | Education |  |  | 1.07
|  |  | Grocery |  |  | 1.02
|  |  | Health |  |  | 1.09
|  |  | Hospital |  |  | 1.16
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.23
|  |  | Multifamily |  |  | 1.13
|  |  | Office - Large |  |  | 1.17
|  |  | Office - Small |  |  | 1.1
|  |  | Religious |  |  | 1.12
|  |  | Restaurant |  |  | 1
|  |  | Retail - Large |  |  | 1
|  |  | Retail - Small |  |  | 1.09
|  |  | Warehouse |  |  | 1
|  |  | Nonresidential Average |  |  | 1.06
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [ISR] |  |  |  |  | 100% | N |  | In Servce Rate or the percentage of units rebated that get installed
| [ΔkWhheatpenalty] | [5 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Convenience | Heating Type | Resistance | 0.36 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Education |  |  | 0.45
|  |  | Grocery |  |  | 0.3
|  |  | Health |  |  | 0.35
|  |  | Hospital |  |  | 0.18
|  |  | Industrial |  |  | 0.37
|  |  | Lodging |  |  | 0.19
|  |  | Multifamily |  |  | 0.44
|  |  | Office - Large |  |  | 0.29
|  |  | Office - Small |  |  | 0.33
|  |  | Religious |  |  | 0.46
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.36
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.24
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
|  |  | Convenience |  | Heat Pump | 0.16
|  |  | Education |  |  | 0.2
|  |  | Grocery |  |  | 0.13
|  |  | Health |  |  | 0.15
|  |  | Hospital |  |  | 0.08
|  |  | Industrial |  |  | 0.16
|  |  | Lodging |  |  | 0.08
|  |  | Multifamily |  |  | 0.19
|  |  | Office - Large |  |  | 0.13
|  |  | Office - Small |  |  | 0.15
|  |  | Religious |  |  | 0.2
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.16
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.1
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [MidLifeAdj] | Lamp Type | 1-Lamp 32w HPT8 (BF < 0.79) |  |  | 84% | C |  | A midlife savings adjustment should be applied to any measure with a blended T12:Standard T8 baseline. The adjustment should occur in 2020 to account for the baseline lamp replacement assumption changing from a blended 50/50 Standard T8/T12 to 100% Standard T8 by 2020.
|  |  | 2-Lamp 32w HPT8 (BF < 0.77) |  |  | 78%
|  |  | 3-Lamp 32w HPT8 (BF < 0.76) |  |  | 53%
|  |  | 4-Lamp 32w HPT8 (BF < 0.78) |  |  | 48%
|  |  | 6-Lamp 32w HPT8 (BF < 0.76) |  |  | 53%
|  |  | 1-Lamp 28w RWT8 (BF < 0.76) |  |  | 89%
|  |  | 2-Lamp 28w RWT8 (BF < 0.76) |  |  | 85%
|  |  | 3-Lamp 28w RWT8 (BF < 0.77) |  |  | 65%
|  |  | 4-Lamp 28w RWT8 (BF < 0.79) |  |  | 61%
|  |  | 6-Lamp 28w RWT8 (BF < 0.77) |  |  | 65%
| [WattsT8Base] | Lamp Type | 1-Lamp 32w HPT8 (BF < 0.79) |  |  | 29 | N |  | Input wattage of the existing system based on 100% T8 fixture
|  |  | 2-Lamp 32w HPT8 (BF < 0.77) |  |  | 57
|  |  | 3-Lamp 32w HPT8 (BF < 0.76) |  |  | 84
|  |  | 4-Lamp 32w HPT8 (BF < 0.78) |  |  | 113
|  |  | 6-Lamp 32w HPT8 (BF < 0.76) |  |  | 169
|  |  | 1-Lamp 28w RWT8 (BF < 0.76) |  |  | 29
|  |  | 2-Lamp 28w RWT8 (BF < 0.76) |  |  | 57
|  |  | 3-Lamp 28w RWT8 (BF < 0.77) |  |  | 84
|  |  | 4-Lamp 28w RWT8 (BF < 0.79) |  |  | 113
|  |  | 6-Lamp 28w RWT8 (BF < 0.77) |  |  | 169
| [WHFd] | Building Type | Convenience |  |  | 1.31 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Education |  |  | 1.48
|  |  | Grocery |  |  | 1.2
|  |  | Health |  |  | 1.69
|  |  | Hospital |  |  | 1.26
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.47
|  |  | Multifamily |  |  | 1.15
|  |  | Office - Large |  |  | 1.04
|  |  | Office - Small |  |  | 1.28
|  |  | Religious |  |  | 1.32
|  |  | Restaurant |  |  | 1.47
|  |  | Retail - Large |  |  | 1.28
|  |  | Retail - Small |  |  | 1.2
|  |  | Warehouse |  |  | 1.19
|  |  | Nonresidential Average |  |  | 1.28
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [CF] | Building Type | Convenience |  |  | 100% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Education |  |  | 65.27%
|  |  | Grocery |  |  | 82.11%
|  |  | Health |  |  | 67%
|  |  | Hospital |  |  | 55.95%
|  |  | Industrial |  |  | 91.8%
|  |  | Lodging |  |  | 61.07%
|  |  | Multifamily |  |  | 71.17%
|  |  | Office - Large |  |  | 60.2%
|  |  | Office - Small |  |  | 51.79%
|  |  | Religious |  |  | 66%
|  |  | Restaurant |  |  | 100%
|  |  | Retail - Large |  |  | 100%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 61.8%
|  |  | Nonresidential Average |  |  | 69.07%
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [IFTherms] | Building Type | Convenience |  |  | 0.015 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Education |  |  | 0.19
|  |  | Grocery |  |  | 0.013
|  |  | Health |  |  | 0.015
|  |  | Hospital |  |  | 0.008
|  |  | Industrial |  |  | 0.016
|  |  | Lodging |  |  | 0.008
|  |  | Multifamily |  |  | 0.019
|  |  | Office - Large |  |  | 0.013
|  |  | Office - Small |  |  | 0.014
|  |  | Religious |  |  | 0.02
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.015
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.01
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [ΔTherms] | [5 empty] | C | Therms | Therm impact calculated above
| [HeatDays] |  |  |  |  | 197 | N | Days | Heat season days per year

## Metal Halide
Metal Halide
| Measure Code: | NR-LTG-PSMH-V02-180101
Note: This measure is effective until 12/31/2017. It should not be used beyond that date but is left in the manual for reference purposes.
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
267
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Custom Calculation
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =(([Watts_Base] - [Watts_EE[) / [1,000] * [Hours] * [WHFe] * [ISR]) + [ΔkWhheatpenalty]
| Time of Sale Demand (ΔkW) | =([Watts_Base] - [Watts_EE]) / [1,000] * [ISR] * [WHFd] * [CF]
| Time of Sale Gas (ΔTherms) | = ([Watts_Base] - [Watts_EE]) / [1,000] * [ISR] * [Hours] * ([- IFTherms])
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([Watts_Base] - [Watts_EE]) / [1,000] * [ISR] * [Hours] * ([-IFkWh])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Lamp Watts EE | Pulse Start MH 150W | Lamp Watts Base | Probe Start MH 175W | 210 | Y |  | Input wattage of the existing system which depends on the baseline fixture configuration (number and type of lamp)
|  |  | Pulse Start MH 175W |  |  | 210
|  |  | Pulse Start MH 200W |  | Probe Start MH250W | 295
|  |  | Pulse Start MH 250W |  |  | 295
|  |  | Pulse Start MH 320W |  | Probe Start MH400W | 458
|  |  | Pulse Start MH350W |  |  | 458
|  |  | Pulse Start MH 400W |  |  | 458
| [WattsEE] | Lamp Watts EE | Pulse Start MH 150W |  |  | 185 | Y |  | New Input wattage of EE fixture, which depends on new fixture configuration
|  |  | Pulse Start MH 175W |  |  | 208
|  |  | Pulse Start MH 200W |  |  | 232
|  |  | Pulse Start MH 250W |  |  | 290
|  |  | Pulse Start MH 320W |  |  | 368
|  |  | Pulse Start MH350W |  |  | 400
|  |  | Pulse Start MH 400W |  |  | 452
| [Hours] | Building Type | Convenience |  |  | 4630 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Education |  |  | 1877
|  |  | Grocery |  |  | 4663
|  |  | Health |  |  | 3806
|  |  | Hospital |  |  | 6520
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3061
|  |  | Multifamily |  |  | 3061
|  |  | Office - Large |  |  | 2920
|  |  | Office - Small |  |  | 2920
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 5443
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 3694
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 3065
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [WHFe] | Building Type | Convenience |  |  | 1.14 | N | Hours | Waste heat factors for energy to account for cooling energy savings from efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Education |  |  | 1.07
|  |  | Grocery |  |  | 1.02
|  |  | Health |  |  | 1.09
|  |  | Hospital |  |  | 1.16
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.23
|  |  | Multifamily |  |  | 1.13
|  |  | Office - Large |  |  | 1.17
|  |  | Office - Small |  |  | 1.1
|  |  | Religious |  |  | 1.12
|  |  | Restaurant |  |  | 1
|  |  | Retail - Large |  |  | 1
|  |  | Retail - Small |  |  | 1.09
|  |  | Warehouse |  |  | 1
|  |  | Nonresidential Average |  |  | 1.06
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [ISR] |  |  |  |  | 97% | N |  | In Service Rate or percentage of units rebated that get installed
| [ΔkWhheatpenalty] | [5 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Convenience | Heating Type | Resistance | 0.36 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Education |  |  | 0.45
|  |  | Grocery |  |  | 0.3
|  |  | Health |  |  | 0.35
|  |  | Hospital |  |  | 0.18
|  |  | Industrial |  |  | 0.37
|  |  | Lodging |  |  | 0.19
|  |  | Multifamily |  |  | 0.44
|  |  | Office - Large |  |  | 0.29
|  |  | Office - Small |  |  | 0.33
|  |  | Religious |  |  | 0.46
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.36
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.24
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
|  |  | Convenience |  | Heat Pump | 0.16
|  |  | Education |  |  | 0.2
|  |  | Grocery |  |  | 0.13
|  |  | Health |  |  | 0.15
|  |  | Hospital |  |  | 0.08
|  |  | Industrial |  |  | 0.16
|  |  | Lodging |  |  | 0.08
|  |  | Multifamily |  |  | 0.19
|  |  | Office - Large |  |  | 0.13
|  |  | Office - Small |  |  | 0.15
|  |  | Religious |  |  | 0.2
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.16
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.1
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [WHFd] | Building Type | Convenience |  |  | 1.31 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Education |  |  | 1.48
|  |  | Grocery |  |  | 1.2
|  |  | Health |  |  | 1.69
|  |  | Hospital |  |  | 1.26
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.47
|  |  | Multifamily |  |  | 1.15
|  |  | Office - Large |  |  | 1.04
|  |  | Office - Small |  |  | 1.28
|  |  | Religious |  |  | 1.32
|  |  | Restaurant |  |  | 1.47
|  |  | Retail - Large |  |  | 1.28
|  |  | Retail - Small |  |  | 1.2
|  |  | Warehouse |  |  | 1.19
|  |  | Nonresidential Average |  |  | 1.28
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [CF] | Building Type | Convenience |  |  | 100% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Education |  |  | 65.27%
|  |  | Grocery |  |  | 82.11%
|  |  | Health |  |  | 67%
|  |  | Hospital |  |  | 55.95%
|  |  | Industrial |  |  | 91.8%
|  |  | Lodging |  |  | 61.07%
|  |  | Multifamily |  |  | 71.17%
|  |  | Office - Large |  |  | 60.2%
|  |  | Office - Small |  |  | 51.79%
|  |  | Religious |  |  | 66%
|  |  | Restaurant |  |  | 100%
|  |  | Retail - Large |  |  | 100%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 61.8%
|  |  | Nonresidential Average |  |  | 69.07%
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [IFTherms] | Building Type | Convenience |  |  | 0.015 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Education |  |  | 0.19
|  |  | Grocery |  |  | 0.013
|  |  | Health |  |  | 0.015
|  |  | Hospital |  |  | 0.008
|  |  | Industrial |  |  | 0.016
|  |  | Lodging |  |  | 0.008
|  |  | Multifamily |  |  | 0.019
|  |  | Office - Large |  |  | 0.013
|  |  | Office - Small |  |  | 0.014
|  |  | Religious |  |  | 0.02
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.015
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.01
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [Δtherms] | [5 empty] | C | therms | Therm impact calcuated above
| [HeatDays] |  |  |  |  | 197 | N |  | Heat season days per year

## Commercial LED Exit Sign
Commercial LED Exit Sign
| Measure Code: | NR-LTG-EXIT-V04-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
13
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Costs known? | Known |  | Actual
|  | Unknown |  | 32.5
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
| RF / DI Program |  | 0.57 | 13
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =(([WattsBase] - [Watts_EE]) / [1,000] * [Hours] * [WHFe]) + [ΔkWhheatpenalty]
| Time of Sale Demand (ΔkW) | =([Watts_Base] - [Watts_EE]) / [1,000] * [WHFd] * [CF]
| Time of Sale Gas (ΔTherms) | = ([Watts_Base] - [Watts_EE]) / [1,000] * [Hours] * ([- IFTherms])
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([Watts_Base] - [Watts_EE]) / [1,000] * [Hours] * ([-IFkWh])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Program Type | Retrofit/Direct Install | Baseline Type | CFL (dual sided) | 14 | Y | Watts | Actual wattage if known
[5 empty] | CFL (single sided) | 7
| [WattsEE] | Single v Dual Sided | Single Sided |  |  | 2 | Y | Watts | Actual wattage if known,
|  |  | Dual Sided |  |  | 4
| [Hours] |  |  |  |  | 8766 | N | Hours | Annual operating hours
| [WHFe] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 1 | N | Hours | Waste heat factors for energy to account for cooling energy savings from efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Convenience |  |  | 1.14
|  |  | Education |  |  | 1.07
|  |  | Exterior Lighting |  |  | 1
|  |  | Grocery |  |  | 1.02
|  |  | Health |  |  | 1.09
|  |  | Hospital |  |  | 1.16
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.23
|  |  | Multifamily |  |  | 1.13
|  |  | Office - Large |  |  | 1.17
|  |  | Office - Small |  |  | 1.1
|  |  | Religious |  |  | 1.12
|  |  | Restaurant |  |  | 1
|  |  | Retail - Large |  |  | 1
|  |  | Retail - Small |  |  | 1.09
|  |  | Warehouse |  |  | 1
|  |  | Nonresidential Average |  |  | 1.06
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [ΔkWhheatpenalty] | [5 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Agricultural Animal Housing and Warehousing | Heating Type | Resistance | 0 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Convenience |  |  | 0.36
|  |  | Education |  |  | 0.45
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.3
|  |  | Health |  |  | 0.35
|  |  | Hospital |  |  | 0.18
|  |  | Industrial |  |  | 0.37
|  |  | Lodging |  |  | 0.19
|  |  | Multifamily |  |  | 0.44
|  |  | Office - Large |  |  | 0.29
|  |  | Office - Small |  |  | 0.33
|  |  | Religious |  |  | 0.46
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.36
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.24
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
|  |  | Agricultural Animal Housing and Warehousing |  | Heat Pump | 0
|  |  | Convenience |  |  | 0.16
|  |  | Education |  |  | 0.2
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.13
|  |  | Health |  |  | 0.15
|  |  | Hospital |  |  | 0.08
|  |  | Industrial |  |  | 0.16
|  |  | Lodging |  |  | 0.08
|  |  | Multifamily |  |  | 0.19
|  |  | Office - Large |  |  | 0.13
|  |  | Office - Small |  |  | 0.15
|  |  | Religious |  |  | 0.2
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.16
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.1
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [WHFd] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 1 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Convenience |  |  | 1.31
|  |  | Education |  |  | 1.48
|  |  | Exterior Lighting |  |  | 1
|  |  | Grocery |  |  | 1.2
|  |  | Health |  |  | 1.69
|  |  | Hospital |  |  | 1.26
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.47
|  |  | Multifamily |  |  | 1.15
|  |  | Office - Large |  |  | 1.04
|  |  | Office - Small |  |  | 1.28
|  |  | Religious |  |  | 1.32
|  |  | Restaurant |  |  | 1.47
|  |  | Retail - Large |  |  | 1.28
|  |  | Retail - Small |  |  | 1.2
|  |  | Warehouse |  |  | 1.19
|  |  | Nonresidential Average |  |  | 1.28
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [CF] |  |  |  |  | 1 | N |  | Summer Peak Coincidence Factor for this measure
| [IFTherms] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 0 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Convenience |  |  | 0.015
|  |  | Education |  |  | 0.019
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.013
|  |  | Health |  |  | 0.015
|  |  | Hospital |  |  | 0.008
|  |  | Industrial |  |  | 0.016
|  |  | Lodging |  |  | 0.008
|  |  | Multifamily |  |  | 0.019
|  |  | Office - Large |  |  | 0.013
|  |  | Office - Small |  |  | 0.014
|  |  | Religious |  |  | 0.02
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.015
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.01
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [Δtherms] | [5 empty] | C | therms | Therm impact calcuated above
| [HeatDays] |  |  |  |  | 197 | N |  | Heat season days per year

## LED Street Lighting
LED Street Lighting
| Measure Code: | NR-LTG-STLT-V01-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
20
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Fixture Type | Decorative/Post Top | Low (<50W) | min | 350
|  | Cobrahead |  |  | 99
|  | Decorative/Post Top |  | max | 615
|  | Cobrahead |  |  | 225
|  | Decorative/Post Top | Med (50W-100W) | min | 550
|  | Cobrahead |  |  | 179
|  | Decorative/Post Top |  | max | 950
|  | Cobrahead |  |  | 451
|  | Decorative/Post Top | High (>100W) | min | 750
|  | Cobrahead |  |  | 310
|  | Decorative/Post Top |  | max | 1450
|  | Cobrahead |  |  | 720
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
| LED Luminaire |  | 1 | 50
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([Watts_Base] - [Watts_EE]) / [1,000] * [Hours]
| Time of Sale Demand (ΔkW) | =([Watts_Base] - [Watts_EE]) / [1,000] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [WattsBase] | Medal Halide |  |  |  | 250 | Y | Watts | Actual wattage is known
|  | Mercury Vapor |  |  |  | 175
|  | High Pressure Sodium |  |  |  | 170
| [WattsEE] | [5 empty] | Y | Watts | Actual wattage
| [Hours] |  |  |  |  | 4100 | N | Hours | Annual operating hours
| [CF] |  |  |  |  | 0% | N |  | Summer Peak Coincidence Factor

## LED Traffic Ped. Signal
LED Traffic Ped. Signal
| Measure Code: | NR-LTG-LDTP-V01-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
10
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([Watts_Base] - [Watts_EE]) / [1,000] * [Hours]
| Time of Sale Demand (ΔkW) | =([Watts_Base] - [Watts_EE]) / [1,000] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Watts_Base] | Round Signals | 8" Red |  |  | 69 | N | Watts | The connected load of the baseline equipment
|  |  | 12" Red |  |  | 150
|  |  | 8" Yellow |  |  | 69
|  |  | 12" Yellow |  |  | 150
|  |  | 8" Green |  |  | 69
|  |  | 12" Green |  |  | 150
|  | Flashing Signal | 8" Red |  |  | 69
|  |  | 12" Red |  |  | 150
|  |  | 8" Yellow |  |  | 69
|  |  | 12" Yellow |  |  | 150
|  | Turn Arrows | 8" Yellow |  |  | 116
|  |  | 12" Yellow |  |  | 116
|  |  | 8" Green |  |  | 116
|  |  | 12" Green |  |  | 116
|  | Pedestrian Sign | 12" Hand/Man |  |  | 116
| [Watts_EE] | Round Signals | 8" Red |  |  | 7 | N | Watts | The connected load of the baseline equipment
|  |  | 12" Red |  |  | 6
|  |  | 8" Yellow |  |  | 10
|  |  | 12" Yellow |  |  | 13
|  |  | 8" Green |  |  | 9
|  |  | 12" Green |  |  | 12
|  | Flashing Signal | 8" Red |  |  | 7
|  |  | 12" Red |  |  | 6
|  |  | 8" Yellow |  |  | 10
|  |  | 12" Yellow |  |  | 13
|  | Turn Arrows | 8" Yellow |  |  | 7
|  |  | 12" Yellow |  |  | 9
|  |  | 8" Green |  |  | 7
|  |  | 12" Green |  |  | 7
|  | Pedestrian Sign | 12" Hand/Man |  |  | 8
| [Hours] | Round Signals | 8" Red |  |  | 4820 | N | Hours | Annual operating hours of the lamp
|  |  | 12" Red |  |  | 4820
|  |  | 8" Yellow |  |  | 175
|  |  | 12" Yellow |  |  | 175
|  |  | 8" Green |  |  | 3675
|  |  | 12" Green |  |  | 3675
|  | Flashing Signal | 8" Red |  |  | 4380
|  |  | 12" Red |  |  | 4380
|  |  | 8" Yellow |  |  | 4380
|  |  | 12" Yellow |  |  | 4380
|  | Turn Arrows | 8" Yellow |  |  | 701
|  |  | 12" Yellow |  |  | 701
|  |  | 8" Green |  |  | 940
|  |  | 12" Green |  |  | 940
|  | Pedestrian Sign | 12" Hand/Man |  |  | 8760
| [CF] | Lamp Type | Red Round, always changing or flashing |  |  | 0.55 | N |  | Peak coincidence factor for measure
|  |  | Red Arrows |  |  | 0.9
|  |  | Green Arrows |  |  | 0.1
|  |  | Yellow Arrows |  |  | 0.03
|  |  | Green Round, always changing or flashing |  |  | 0.43
|  |  | Flashing Yellow |  |  | 0.5
|  |  | Yellow Round, always changing |  |  | 0.02
|  |  | “Hand” Don’t Walk Signal |  |  | 0.75
|  |  | “Man” Walk Signal |  |  | 0.21

## Lighting Controls
Lighting Controls
| Measure Code: | NR-LTG-LICO-V01-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
8
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Type | Switch-Mounted (Wall) Occupancy Sensor |  | 54
|  | Fixture-Mounted Occupancy Sensor |  | 67
|  | Remote-Mounted (Ceiling) Occupancy Sensor |  | 105
|  | Fixture-Mounted Daylight Sensor |  | 50
|  | Remote-Mounted Daylight Sensor |  | 65
|  | Integrated Occupancy Sensor |  | 40
|  | Integrated Dual Occupancy & Daylight Sensor |  | 50
|  | Fixture-Mounted Dual Occupancy & Daylight Sensor |  | 100
|  | Remote-Mounted Dual Occupancy & Daylight Sensor |  | 125
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [kW_Controlled] *[Hours] * [ESF] * [WHFe]
| Time of Sale Demand (ΔkW) | = [kW_Controlled] * [WHFd] * ([CFbaseline] – [CFLC])
| Time of Sale Gas (ΔTherms) | = [kW_Controlled] * [Hours] * [ESF] * - [IFTherms]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [Heatdays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([WattsBase] - [WattsEE]) / [1,000] * [ISR] * [Hours] * (-[IFkWh])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [kWControlled] | Lighting Control Type Interior | Switch (wall) mounted occupancy sensor |  |  | 0.254 | Y | kW | Total lighting load connected to the control in kilowatts. Savings is per control. The total connected load per control should be collected from the customer, or use the default values presented
|  |  | Fixture-mounted occupancy sensor |  |  | 0.264
|  |  | Remote (ceiling) mounted occupancy sensor |  |  | 0.413
|  |  | Fixture-Mounted Daylight Sensor |  |  | 0.095
|  |  | Remote-Mounted Daylight Sensor |  |  | 0.239
|  |  | Integrated Occupancy Sensor for LED Interior Fixtures < 10,000 Lumens |  |  | 0.031
|  |  | Integrated Occupancy Sensor for LED Interior Fixtures ≥ 10,000 Lumens |  |  | 0.118
|  |  | Integrated Dual Occupancy & Daylight Sensor for LED Interior Fixtures < 10,000 Lumens |  |  | 0.031
|  |  | Integrated Dual Occupancy & Daylight Sensor for LED Interior Fixtures ≥ 10,000 Lumens |  |  | 0.118
|  |  | Fixture-Mounted Dual Occupancy & Daylight Sensor for LED Interior Fixtures |  |  | 0.031
|  |  | < 10,000 Lumens |  |  | 0.118
|  |  | Fixture-Mounted Dual Occupancy & Daylight Sensor for LED Interior Fixtures |  |  | 0.239
| [Hours] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 2920 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Convenience |  |  | 4630
|  |  | Education |  |  | 1877
|  |  | Exterior Lighting |  |  | 4676
|  |  | Grocery |  |  | 4663
|  |  | Health |  |  | 3806
|  |  | Hospital |  |  | 6520
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3061
|  |  | Multifamily |  |  | 3061
|  |  | Office - Large |  |  | 2920
|  |  | Office - Small |  |  | 2920
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 5443
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 3694
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 3065
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [ESF] | Lighting Control Type Interior | Daylighting |  |  | 28% | Y |  | Energy Savings factor (represents the percentage reduction to the operating Hours from the non-controlled baseline lighting system). Determined on a site-specific basis or using the default values
|  |  | Occupancy Sensor |  |  | 24%
|  |  | Dual Sensor with verified daylighting |  |  | 24%
|  |  | Dual Sensor without verified daylighting |  |  | 38%
| [WHFe] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 1 | N | Hours | Waste heat factors for energy to account for cooling energy savings from efficient lighting
|  |  | Convenience |  |  | 1.14
|  |  | Education |  |  | 1.07
|  |  | Exterior Lighting |  |  | 1
|  |  | Grocery |  |  | 1.02
|  |  | Health |  |  | 1.09
|  |  | Hospital |  |  | 1.16
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.23
|  |  | Multifamily |  |  | 1.13
|  |  | Office - Large |  |  | 1.17
|  |  | Office - Small |  |  | 1.1
|  |  | Religious |  |  | 1.12
|  |  | Restaurant |  |  | 1
|  |  | Retail - Large |  |  | 1
|  |  | Retail - Small |  |  | 1.09
|  |  | Warehouse |  |  | 1
|  |  | Nonresidential Average |  |  | 1.06
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [ΔkWhheatpenalty] | [5 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Agricultural Animal Housing and Warehousing | Heating Type | Resistance | 0 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Convenience |  |  | 0.36
|  |  | Education |  |  | 0.45
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.3
|  |  | Health |  |  | 0.35
|  |  | Hospital |  |  | 0.18
|  |  | Industrial |  |  | 0.37
|  |  | Lodging |  |  | 0.19
|  |  | Multifamily |  |  | 0.44
|  |  | Office - Large |  |  | 0.29
|  |  | Office - Small |  |  | 0.33
|  |  | Religious |  |  | 0.46
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.36
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.24
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
|  |  | Agricultural Animal Housing and Warehousing |  | Heat Pump | 0
|  |  | Convenience |  |  | 0.16
|  |  | Education |  |  | 0.2
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.13
|  |  | Health |  |  | 0.15
|  |  | Hospital |  |  | 0.08
|  |  | Industrial |  |  | 0.16
|  |  | Lodging |  |  | 0.08
|  |  | Multifamily |  |  | 0.19
|  |  | Office - Large |  |  | 0.13
|  |  | Office - Small |  |  | 0.15
|  |  | Religious |  |  | 0.2
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.16
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.1
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [WHFd] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 1 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Convenience |  |  | 1.31
|  |  | Education |  |  | 1.48
|  |  | Exterior Lighting |  |  | 1
|  |  | Grocery |  |  | 1.2
|  |  | Health |  |  | 1.69
|  |  | Hospital |  |  | 1.26
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.47
|  |  | Multifamily |  |  | 1.15
|  |  | Office - Large |  |  | 1.04
|  |  | Office - Small |  |  | 1.28
|  |  | Religious |  |  | 1.32
|  |  | Restaurant |  |  | 1.47
|  |  | Retail - Large |  |  | 1.28
|  |  | Retail - Small |  |  | 1.2
|  |  | Warehouse |  |  | 1.19
|  |  | Nonresidential Average |  |  | 1.28
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [CFbaseline] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 61.8% | N |  | Baseline Summer Peak Coincidence Factor for the lighting system without Occupancy Sensors installed is selected from the Lighting Reference Table in Section 3.4 for each building type. If the building type is unknown, use the Nonresidential Average value.
|  |  | Convenience |  |  | 100%
|  |  | Education |  |  | 65.27%
|  |  | Exterior Lighting |  |  | 0%
|  |  | Grocery |  |  | 82.11%
|  |  | Health |  |  | 67%
|  |  | Hospital |  |  | 55.95%
|  |  | Industrial |  |  | 91.8%
|  |  | Lodging |  |  | 61.07%
|  |  | Multifamily |  |  | 71.17%
|  |  | Office - Large |  |  | 60.2%
|  |  | Office - Small |  |  | 51.79%
|  |  | Religious |  |  | 66%
|  |  | Restaurant |  |  | 100%
|  |  | Retail - Large |  |  | 100%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 61.8%
|  |  | Nonresidential Average |  |  | 69.07%
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [CFLC] |  |  |  |  | 0.15 | N |  | Retrofit Summer Peak Coincidence Factor the lighting system with lighting control installed
| [IFTherms] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 0 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Convenience |  |  | 0.015
|  |  | Education |  |  | 0.019
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.013
|  |  | Health |  |  | 0.015
|  |  | Hospital |  |  | 0.008
|  |  | Industrial |  |  | 0.016
|  |  | Lodging |  |  | 0.008
|  |  | Multifamily |  |  | 0.019
|  |  | Office - Large |  |  | 0.013
|  |  | Office - Small |  |  | 0.014
|  |  | Religious |  |  | 0.02
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.015
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.01
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [ΔTherms] | [5 empty] | C | Therms | Therm impact calculated above
| [HeatDays] |  |  |  |  | 197 | N | Days | Heat season days per year

## Daylighting Control
Daylighting Control
| Measure Code: | NR-LTG-DAYC-V03-200101
Measure now combined in to Lighting Control measure
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
8
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Photosensor Control Type | Fixture-mounted dalylight sensor (per ballast controlled) | 50
|  | Remote-mounted daylight sensor (per ballast controlled) | 65
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = ([kW_Controlled] * [Hours] * [ESF] * [WHFe]) + [ΔkWhheatpenalty]
| Time of Sale Demand (ΔkW) | = [kW_Controlled] * [WHFd] * [CF]
| Time of Sale Gas (ΔTherms) | = [kW_Controlled] * [Hours] * [ESF] * ([- IFTherms])
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | = [kW_Controlled] * [Hours] * [ESF] * ([-IFkWh])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [kWControlled] | Lighting Control Type | Fixture-mounted dalylight sensor (per ballast controlled) |  |  | 0.073 | Y | kW | Total lighting load connected to the control in kilowatts. Savings is an average per control or ballast as outlined below.
|  |  | Remote-mounted daylight sensor (per ballast controlled) |  |  | 0.35
| [Hours] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 2920 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Convenience |  |  | 4630
|  |  | Education |  |  | 1877
|  |  | Exterior Lighting |  |  | 4676
|  |  | Grocery |  |  | 4663
|  |  | Health |  |  | 3806
|  |  | Hospital |  |  | 6520
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3061
|  |  | Multifamily |  |  | 3061
|  |  | Office - Large |  |  | 2920
|  |  | Office - Small |  |  | 2920
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 5443
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 3694
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 3065
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [ESF] |  |  |  |  | 28% | Y |  | Energy Savings factor (represents the percentage reduction to the operating Hours from the non-controlled baseline lighting system).
| [WHFe] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 1 | N |  | Waste heat factors for energy to account for cooling energy savings from efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Convenience |  |  | 1.14
|  |  | Education |  |  | 1.07
|  |  | Exterior Lighting |  |  | 1
|  |  | Grocery |  |  | 1.02
|  |  | Health |  |  | 1.09
|  |  | Hospital |  |  | 1.16
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.23
|  |  | Multifamily |  |  | 1.13
|  |  | Office - Large |  |  | 1.17
|  |  | Office - Small |  |  | 1.1
|  |  | Religious |  |  | 1.12
|  |  | Restaurant |  |  | 1
|  |  | Retail - Large |  |  | 1
|  |  | Retail - Small |  |  | 1.09
|  |  | Warehouse |  |  | 1
|  |  | Nonresidential Average |  |  | 1.06
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [ΔkWhheatpenalty] | [5 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Agricultural Animal Housing and Warehousing | Heating Type | Resistance | 0 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Convenience |  |  | 0.36
|  |  | Education |  |  | 0.45
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.3
|  |  | Health |  |  | 0.35
|  |  | Hospital |  |  | 0.18
|  |  | Industrial |  |  | 0.37
|  |  | Lodging |  |  | 0.19
|  |  | Multifamily |  |  | 0.44
|  |  | Office - Large |  |  | 0.29
|  |  | Office - Small |  |  | 0.33
|  |  | Religious |  |  | 0.46
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.36
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.24
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
|  |  | Agricultural Animal Housing and Warehousing |  | Heat Pump | 0
|  |  | Convenience |  |  | 0.16
|  |  | Education |  |  | 0.2
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.13
|  |  | Health |  |  | 0.15
|  |  | Hospital |  |  | 0.08
|  |  | Industrial |  |  | 0.16
|  |  | Lodging |  |  | 0.08
|  |  | Multifamily |  |  | 0.19
|  |  | Office - Large |  |  | 0.13
|  |  | Office - Small |  |  | 0.15
|  |  | Religious |  |  | 0.2
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.16
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.1
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [WHFd] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 1 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Convenience |  |  | 1.31
|  |  | Education |  |  | 1.48
|  |  | Exterior Lighting |  |  | 1
|  |  | Grocery |  |  | 1.2
|  |  | Health |  |  | 1.69
|  |  | Hospital |  |  | 1.26
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.47
|  |  | Multifamily |  |  | 1.15
|  |  | Office - Large |  |  | 1.04
|  |  | Office - Small |  |  | 1.28
|  |  | Religious |  |  | 1.32
|  |  | Restaurant |  |  | 1.47
|  |  | Retail - Large |  |  | 1.28
|  |  | Retail - Small |  |  | 1.2
|  |  | Warehouse |  |  | 1.19
|  |  | Nonresidential Average |  |  | 1.28
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [CF] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 61.8% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Convenience |  |  | 100%
|  |  | Education |  |  | 65.27%
|  |  | Exterior Lighting |  |  | 0%
|  |  | Grocery |  |  | 82.11%
|  |  | Health |  |  | 67%
|  |  | Hospital |  |  | 55.95%
|  |  | Industrial |  |  | 91.8%
|  |  | Lodging |  |  | 61.07%
|  |  | Multifamily |  |  | 71.17%
|  |  | Office - Large |  |  | 60.2%
|  |  | Office - Small |  |  | 51.79%
|  |  | Religious |  |  | 66%
|  |  | Restaurant |  |  | 100%
|  |  | Retail - Large |  |  | 100%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 61.8%
|  |  | Nonresidential Average |  |  | 69.07%
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [IFTherms] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 0 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Convenience |  |  | 0.015
|  |  | Education |  |  | 0.019
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.013
|  |  | Health |  |  | 0.015
|  |  | Hospital |  |  | 0.008
|  |  | Industrial |  |  | 0.016
|  |  | Lodging |  |  | 0.008
|  |  | Multifamily |  |  | 0.019
|  |  | Office - Large |  |  | 0.013
|  |  | Office - Small |  |  | 0.014
|  |  | Religious |  |  | 0.02
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.015
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.01
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [Δtherms] | [5 empty] | C | therms | Therm impact calcuated above
| [HeatDays] |  |  |  |  | 197 | N |  | Heat season days per year

## Multilevel Lighting Switch
Multilevel Lighting Switch
| Measure Code: | NR-LTG-MLLS-V03-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
10
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
274
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = ([kW_Controlled] * [Hours] * [ESF] * [WHFe]) + [ΔkWhheatpenalty]
| Time of Sale Demand (ΔkW) | = [kW_Controlled] * [ESF] * [WHFd] * [CF]
| Time of Sale Gas (ΔTherms) | = [kW_Controlled] * [Hours] * [ESF] * ([- IFTherms])
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | = [kW_Controlled] * [Hours] * [ESF] * ([-IFkWh])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [KWControlled] | [5 empty] | Y | kW | Total lighting load connected to the control in kW
| [Hours] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 2920 | N | Hours | Average hours of use per year, if unknown, use the Nonresidential Average value
|  |  | Convenience |  |  | 4630
|  |  | Education |  |  | 1877
|  |  | Exterior Lighting |  |  | 4676
|  |  | Grocery |  |  | 4663
|  |  | Health |  |  | 3806
|  |  | Hospital |  |  | 6520
|  |  | Industrial |  |  | 2850
|  |  | Lodging |  |  | 3061
|  |  | Multifamily |  |  | 3061
|  |  | Office - Large |  |  | 2920
|  |  | Office - Small |  |  | 2920
|  |  | Religious |  |  | 2412
|  |  | Restaurant |  |  | 5443
|  |  | Retail - Large |  |  | 4065
|  |  | Retail - Small |  |  | 3694
|  |  | Warehouse |  |  | 2920
|  |  | Nonresidential Average |  |  | 3065
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [ESF] |  |  |  |  | 31% | Y |  | Energy Savings factor (represents the percentage reduction to the operating Hours from the non-controlled baseline lighting system).
| [WHFe] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 1 | N | Hours | Waste heat factors for energy to account for cooling energy savings from efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Convenience |  |  | 1.14
|  |  | Education |  |  | 1.07
|  |  | Exterior Lighting |  |  | 1
|  |  | Grocery |  |  | 1.02
|  |  | Health |  |  | 1.09
|  |  | Hospital |  |  | 1.16
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.23
|  |  | Multifamily |  |  | 1.13
|  |  | Office - Large |  |  | 1.17
|  |  | Office - Small |  |  | 1.1
|  |  | Religious |  |  | 1.12
|  |  | Restaurant |  |  | 1
|  |  | Retail - Large |  |  | 1
|  |  | Retail - Small |  |  | 1.09
|  |  | Warehouse |  |  | 1
|  |  | Nonresidential Average |  |  | 1.06
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [ΔkWhheatpenalty] | [5 empty] | C |  | Heating penalty due to reduced waste heat if electrically heated building
| [IFkWh] | Building Type | Agricultural Animal Housing and Warehousing | Heating Type | Resistance | 0 | N |  | Lighting-HVAC Interaction Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the redution of waste heat rejected by the efficient lighting.
|  |  | Convenience |  |  | 0.36
|  |  | Education |  |  | 0.45
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.3
|  |  | Health |  |  | 0.35
|  |  | Hospital |  |  | 0.18
|  |  | Industrial |  |  | 0.37
|  |  | Lodging |  |  | 0.19
|  |  | Multifamily |  |  | 0.44
|  |  | Office - Large |  |  | 0.29
|  |  | Office - Small |  |  | 0.33
|  |  | Religious |  |  | 0.46
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.36
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.24
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
|  |  | Agricultural Animal Housing and Warehousing |  | Heat Pump | 0
|  |  | Convenience |  |  | 0.16
|  |  | Education |  |  | 0.2
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.13
|  |  | Health |  |  | 0.15
|  |  | Hospital |  |  | 0.08
|  |  | Industrial |  |  | 0.16
|  |  | Lodging |  |  | 0.08
|  |  | Multifamily |  |  | 0.19
|  |  | Office - Large |  |  | 0.13
|  |  | Office - Small |  |  | 0.15
|  |  | Religious |  |  | 0.2
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.16
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.1
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [WHFd] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 1 | N |  | Waste heat factor for demand to account for cooling savings from efficient lighting in cooled buildings, if unknown use Nonresidential Average value
|  |  | Convenience |  |  | 1.31
|  |  | Education |  |  | 1.48
|  |  | Exterior Lighting |  |  | 1
|  |  | Grocery |  |  | 1.2
|  |  | Health |  |  | 1.69
|  |  | Hospital |  |  | 1.26
|  |  | Industrial |  |  | 1.02
|  |  | Lodging |  |  | 1.47
|  |  | Multifamily |  |  | 1.15
|  |  | Office - Large |  |  | 1.04
|  |  | Office - Small |  |  | 1.28
|  |  | Religious |  |  | 1.32
|  |  | Restaurant |  |  | 1.47
|  |  | Retail - Large |  |  | 1.28
|  |  | Retail - Small |  |  | 1.2
|  |  | Warehouse |  |  | 1.19
|  |  | Nonresidential Average |  |  | 1.28
|  |  | Unconditioned building |  |  | 1
|  |  | Refrigerated Cases |  |  | 1.29
|  |  | Freezer Cases |  |  | 1.5
| [CF] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 61.8% | N |  | Summer Peak Coincidence Factor, if unknown use the Nonresidential Average value
|  |  | Convenience |  |  | 100%
|  |  | Education |  |  | 65.27%
|  |  | Exterior Lighting |  |  | 0%
|  |  | Grocery |  |  | 82.11%
|  |  | Health |  |  | 67%
|  |  | Hospital |  |  | 55.95%
|  |  | Industrial |  |  | 91.8%
|  |  | Lodging |  |  | 61.07%
|  |  | Multifamily |  |  | 71.17%
|  |  | Office - Large |  |  | 60.2%
|  |  | Office - Small |  |  | 51.79%
|  |  | Religious |  |  | 66%
|  |  | Restaurant |  |  | 100%
|  |  | Retail - Large |  |  | 100%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 61.8%
|  |  | Nonresidential Average |  |  | 69.07%
|  |  | Unconditioned building |  |  | As specific building above
|  |  | Refrigerated Cases |  |  | As specific building above
|  |  | Freezer Cases |  |  | As specific building above
| [IFTherms] | Building Type | Agricultural Animal Housing and Warehousing |  |  | 0 | N |  | Lighting-HVAC Interaction Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the redution of waste heat rejected by the efficient lighting. If unknown, use the Nonresidential Average value.
|  |  | Convenience |  |  | 0.015
|  |  | Education |  |  | 0.019
|  |  | Exterior Lighting |  |  | 0
|  |  | Grocery |  |  | 0.013
|  |  | Health |  |  | 0.015
|  |  | Hospital |  |  | 0.008
|  |  | Industrial |  |  | 0.016
|  |  | Lodging |  |  | 0.008
|  |  | Multifamily |  |  | 0.019
|  |  | Office - Large |  |  | 0.013
|  |  | Office - Small |  |  | 0.014
|  |  | Religious |  |  | 0.02
|  |  | Restaurant |  |  | 0
|  |  | Retail - Large |  |  | 0
|  |  | Retail - Small |  |  | 0.015
|  |  | Warehouse |  |  | 0
|  |  | Nonresidential Average |  |  | 0.01
|  |  | Unconditioned building |  |  | 0
|  |  | Refrigerated Cases |  |  | 0
|  |  | Freezer Cases |  |  | 0
| [Δtherms] | [5 empty] | C | therms | Therm impact calcuated above
| [HeatDays] |  |  |  |  | 197 | N |  | Heat season days per year

## VFDs for Process
VFDs for Process
| Measure Code: | NR-MSC-VFDP-V03-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Costs known? | Known |  |  | Actual - Baseline | Actual
|  | Unknown | Horse Power | 1-9 | 2177
|  |  |  | 10-19 | 3123
|  |  |  | 20-29 | 4280
|  |  |  | 30-39 | 5023
|  |  |  | 40-49 | 5766
|  |  |  | 50-59 | 6591
|  |  |  | 60-69 | 7550
|  |  |  | 70-79 | 8173
|  |  |  | 80-89 | 8796
|  |  |  | 90-100 | 9576
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [HP] * [Hours] * [ESF]
| Time of Sale Demand (ΔkW) | = [HP] * [DSF}
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [HP] | [5 empty] | Y | HP | Nominal horsepower of controlled motor
| [HOURS] | [5 empty] | Y | Hours | Annual operating hours of motor
| [ESF] | Type | Process Fans |  |  | 0.189 | N | kWh/HP | Energy Savings factor
|  |  | Process Centrifugal Pumps |  |  | 0.26
| [DSF] | Type | Process Fans |  |  | 0.16 | N | kW/HP | Demand Savings factor
|  |  | Process Centrifugal Pumps |  |  | 0.26

## Clothes Washer
Clothes Washer
| Measure Code: | NR-MSC-CLWA-V02-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
11
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
190
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =(([Capacity] * 1 / [MEFbase] * [Ncycles]) * ([%Cwbase] + ([%DHWbase] * [%Electric_DHW] )+ ([%Dryerbase] * [%Electric_Dryer]))) - (([Capacity] * 1 / [IMEFeff] * [Ncycles]) * ([%Cweff] + ([%DHWeff] * [%Electric_DHW ]) + ([%Dryereff] * [%Electric_Dryer])))
| Time of Sale Demand (ΔkW) | = [ΔkWh] / [Hours] * [CF]
| Time of Sale Gas (ΔTherms) | =((([Capacity] * 1 / [IMEFbase] * [Ncycles]) * (([%DHWbase] * [%Natural Gas_DHW] * [R_eff]) + ([%Dryerbase] * [%Gas_Dryer%Gas _Dryer]))) - (([Capacity] * 1 / [IMEFeff] * [Ncycles]) * (([%DHWeff] * [%Gas_DHW%Natural Gas_DHW] * [R_eff]) + ([%Dryereff] * [%Gas_Dryer%Gas_Dryer]))) * [Therm_convert]
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] / [365]
| Time of Sale Water (ΔGallons) | = [Capacity * ([IWFbase] - [IWFeff]) * [Ncycles]
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Capacity] |  |  |  |  | 3.3 | Y | ft3 | Clothes Washer capacity
| [MEFbase] | Efficiency Level | Federal Standard | Type | Top Loading | 1.35 | N |  | Modified Efficiency Factor of baseline unit
[5 empty] | Front Loading | 2
[5 empty] | Weighted Average | 1.5
| [MEFeff] | Efficiency Level | ENERGY STAR | Type | Top Loading | 2.2 | Y |  | Modified Energy Factor of efficient unit
Front Loading
Weighted Average
| [Ncycles] |  |  |  |  | 2190 | N |  | Number of Cycles per year
| [%CW] | Federal Standard |  |  |  | 7% | N |  | Percentage of total energy consumption for Clothes Washer operation
|  | ENERGY STAR |  |  |  | 3.9%
| [%DHW] | Federal Standard |  |  |  | 28.1% | N |  | Percentage of total energy consumption used for water heating
|  | ENERGY STAR |  |  |  | 15.5%
| [%Dryer] | Federal Standard |  |  |  | 64.9% | N |  | Percentage of total energy consumption for dryer operation
|  | ENERGY STAR |  |  |  | 80.6%
| [%ElectricDHW] | DWH Fuel | Electric |  |  | 100% | N |  | Percentage of DHW savings assumed to be electric
|  |  | Gas |  |  | 0%
| [%ElectricDryer] | Dryer Fuel | Electric |  |  | 100% | N |  | Percentage of dryer savings assumed to be electric
|  |  | Gas |  |  | 0%
| [ΔkWh] | [5 empty] | C | kWh | Energy savings as calculated above
| [Hours] |  |  |  |  | 1643 | N | Hours | Assumed run hours of clothes washer
| [CF] |  |  |  |  | 0.5 | N |  | Summer peak coincidence factor for measure
| [%GasDHW] | DHW Fuel | Electric |  |  | 0% | N |  | Percentage of DHW savings assumed to be Natural Gas
|  |  | Gas |  |  | 100%
| [R_eff] |  |  |  |  | 1.26 | N |  | Recovery efficiency factor
| [%GasDryer] | Dryer Fuel | Electric |  |  | 0% | N |  | Percentage of dryer savings assumed to be Natural Gas
|  |  | Gas |  |  | 100%
| [Therm_convert] |  |  |  |  | 0.03412 | N | kWh to therm | Conversion factor from kWh to Therm
| [Δtherms] | [5 empty] | C | therms | Therm impact calcuated above
| [365] |  |  |  |  | 365 | N | days | Days per year
| [Δgallons] |  |  |  |  | 19874 | C | gallons | Water savings in gallons
| [IWFbase] | Efficiency Level | Federal Standard | Type | Top Loading | 8.8 | N |  | Water factor of baseline clothes washer
[5 empty] | Front Loading | 4.1
[5 empty] | Weighted Average | 7.5
| [IWFeff] | Efficiency Level | ENERGY STAR | Type | Top Loading | 4 | N |  | Water factor of efficient clothes washer
Front Loading
Weighted Average

## Motors
Motors
| Measure Code: | NR-MCS-MOTR-V03-200101
| Lifetime of Efficient Equipment: | [9 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime | [7 empty] | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
16
| Measure Cost: | [9 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  |  |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known |  |  | Actual - Baseline
|  | Unknown | Horsepower | <=300 hp | $37.98 * (HP rating) + $433.78
|  |  |  | >300hp | $142.48 * (HP rating) - $31,601.70
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([kW_Base] - [kW_EE]) * [Hours]
| Time of Sale Demand (ΔkW) | =([kW_Base] - [kW_EE]) * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [kWbase] |  |  | =([0.746] * [HP] * [LF] / [η_Bmotor])
| [kWee] |  |  | =([0.746] * [HP] * [LF] / [η_Bmotor])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [kW_Base] | [7 empty] | C | kW | Demand of baseline motor
| [kW_EE] | [7 empty] | C | kW | Demand of energy efficient motor
| [0.746] | [6 empty] | 0.746 | N |  | Conversion factor for HP to kWh
| [HP] | [7 empty] | Y | HP | Nominal horsepower of controlled motor
| [LF] | [6 empty] | 75% | Y |  | Load factor; motor load at fan/pump desigh CFM
| [η_Bmotor] | Motor Design Type | NEMA Design A, NEMA Design B and IEC Design N Motors (Excluding Fire Pump Electric Motors) at 60 Hz: | Motor HP/Standard kW Equiv. | 1/0.75 | # of Poles | ODP 8 Poles | 75.5% | N |  | Federal baseline nominal/nameplate motor efficiency for Open Drip Proof (ODP) and Totally Enclosed Fan Cooled (TEFC)
[7 empty] | ODP 6 Poles | 82.5%
[7 empty] | ODP 4 Poles | 85.5%
[7 empty] | ODP 2 Poles | 77%
[5 empty] | 1.5/1.1 |  | ODP 8 Poles | 77%
[7 empty] | ODP 6 Poles | 86.5%
[7 empty] | ODP 4 Poles | 86.5%
[7 empty] | ODP 2 Poles | 84%
[5 empty] | 2/1.5 |  | ODP 8 Poles | 86.5%
[7 empty] | ODP 6 Poles | 87.5%
[7 empty] | ODP 4 Poles | 86.5%
[7 empty] | ODP 2 Poles | 85.5%
[5 empty] | 3/2.2 |  | ODP 8 Poles | 87.5%
[7 empty] | ODP 6 Poles | 88.5%
[7 empty] | ODP 4 Poles | 89.5%
[7 empty] | ODP 2 Poles | 85.5%
[5 empty] | 5/3.7 |  | ODP 8 Poles | 88.5%
[7 empty] | ODP 6 Poles | 89.5%
[7 empty] | ODP 4 Poles | 89.5%
[7 empty] | ODP 2 Poles | 86.5%
[5 empty] | 7.5/5.5 |  | ODP 8 Poles | 89.5%
[7 empty] | ODP 6 Poles | 90.2%
[7 empty] | ODP 4 Poles | 91%
[7 empty] | ODP 2 Poles | 88.5%
[5 empty] | 10/7.5 |  | ODP 8 Poles | 90.2%
[7 empty] | ODP 6 Poles | 91.7%
[7 empty] | ODP 4 Poles | 91.7%
[7 empty] | ODP 2 Poles | 89.5%
[5 empty] | 15 /11 |  | ODP 8 Poles | 90.2%
[7 empty] | ODP 6 Poles | 91.7%
[7 empty] | ODP 4 Poles | 93%
[7 empty] | ODP 2 Poles | 90.2%
[5 empty] | 20 /15 |  | ODP 8 Poles | 91%
[7 empty] | ODP 6 Poles | 92.4%
[7 empty] | ODP 4 Poles | 93%
[7 empty] | ODP 2 Poles | 91%
[5 empty] | 25/18.5 |  | ODP 8 Poles | 91%
[7 empty] | ODP 6 Poles | 93%
[7 empty] | ODP 4 Poles | 93.6%
[7 empty] | ODP 2 Poles | 91.7%
[5 empty] | 30 /22 |  | ODP 8 Poles | 91.7%
[7 empty] | ODP 6 Poles | 93.6%
[7 empty] | ODP 4 Poles | 94.1%
[7 empty] | ODP 2 Poles | 91.7%
[5 empty] | 40 /30 |  | ODP 8 Poles | 91.7%
[7 empty] | ODP 6 Poles | 94.1%
[7 empty] | ODP 4 Poles | 94.1%
[7 empty] | ODP 2 Poles | 92.4%
[5 empty] | 50 /37 |  | ODP 8 Poles | 92.4%
[7 empty] | ODP 6 Poles | 94.1%
[7 empty] | ODP 4 Poles | 94.5%
[7 empty] | ODP 2 Poles | 93%
[5 empty] | 60 /45 |  | ODP 8 Poles | 93%
[7 empty] | ODP 6 Poles | 94.5%
[7 empty] | ODP 4 Poles | 95%
[7 empty] | ODP 2 Poles | 93.6%
[5 empty] | 75 /55 |  | ODP 8 Poles | 94.1%
[7 empty] | ODP 6 Poles | 94.5%
[7 empty] | ODP 4 Poles | 95%
[7 empty] | ODP 2 Poles | 93.6%
[5 empty] | 100 /75 |  | ODP 8 Poles | 94.1%
[7 empty] | ODP 6 Poles | 95%
[7 empty] | ODP 4 Poles | 95.4%
[7 empty] | ODP 2 Poles | 93.6%
[5 empty] | 125 /90 |  | ODP 8 Poles | 94.1%
[7 empty] | ODP 6 Poles | 95%
[7 empty] | ODP 4 Poles | 95.4%
[7 empty] | ODP 2 Poles | 94.1%
[5 empty] | 150 /110 |  | ODP 8 Poles | 94.1%
[7 empty] | ODP 6 Poles | 95.4%
[7 empty] | ODP 4 Poles | 95.8%
[7 empty] | ODP 2 Poles | 94.1%
[5 empty] | 200 /150 |  | ODP 8 Poles | 94.1%
[7 empty] | ODP 6 Poles | 95.4%
[7 empty] | ODP 4 Poles | 95.8%
[7 empty] | ODP 2 Poles | 95%
[5 empty] | 250 /186 |  | ODP 8 Poles | 95%
[7 empty] | ODP 6 Poles | 95.8%
[7 empty] | ODP 4 Poles | 95.8%
[7 empty] | ODP 2 Poles | 95%
[5 empty] | 300 /224 |  | ODP 6 Poles | 95.8%
[7 empty] | ODP 4 Poles | 95.8%
[7 empty] | ODP 2 Poles | 95.4%
[5 empty] | 350 /261 |  | ODP 6 Poles | 95.8%
[7 empty] | ODP 4 Poles | 95.8%
[7 empty] | ODP 2 Poles | 95.4%
[5 empty] | 400 /298 |  | ODP 4 Poles | 95.8%
[7 empty] | ODP 2 Poles | 95.8%
[5 empty] | 450 /336 |  | ODP 4 Poles | 96.2%
[7 empty] | ODP 2 Poles | 96.2%
[5 empty] | 500 /373 |  | ODP 4 Poles | 96.2%
[7 empty] | ODP 2 Poles | 96.2%
[5 empty] | 1/0.75 |  | TEFC 8 Poles | 75.5%
[7 empty] | TEFC 6 Poles | 82.5%
[7 empty] | TEFC 4 Poles | 85.5%
[7 empty] | TEFC 2 Poles | 77%
[5 empty] | 1.5/1.1 |  | TEFC 8 Poles | 78.5%
[7 empty] | TEFC 6 Poles | 87.5%
[7 empty] | TEFC 4 Poles | 86.5%
[7 empty] | TEFC 2 Poles | 84%
[5 empty] | 2/1.5 |  | TEFC 8 Poles | 84%
[7 empty] | TEFC 6 Poles | 88.5%
[7 empty] | TEFC 4 Poles | 86.5%
[7 empty] | TEFC 2 Poles | 85.5%
[5 empty] | 3/2.2 |  | TEFC 8 Poles | 85.5%
[7 empty] | TEFC 6 Poles | 89.5%
[7 empty] | TEFC 4 Poles | 89.5%
[7 empty] | TEFC 2 Poles | 86.5%
[5 empty] | 5/3.7 |  | TEFC 8 Poles | 86.5%
[7 empty] | TEFC 6 Poles | 89.5%
[7 empty] | TEFC 4 Poles | 89.5%
[7 empty] | TEFC 2 Poles | 88.5%
[5 empty] | 7.5/5.5 |  | TEFC 8 Poles | 86.5%
[7 empty] | TEFC 6 Poles | 91%
[7 empty] | TEFC 4 Poles | 91.7%
[7 empty] | TEFC 2 Poles | 89.5%
[5 empty] | 10/7.5 |  | TEFC 8 Poles | 89.5%
[7 empty] | TEFC 6 Poles | 91%
[7 empty] | TEFC 4 Poles | 91.7%
[7 empty] | TEFC 2 Poles | 90.2%
[5 empty] | 15 /11 |  | TEFC 8 Poles | 89.5%
[7 empty] | TEFC 6 Poles | 91.7%
[7 empty] | TEFC 4 Poles | 92.4%
[7 empty] | TEFC 2 Poles | 91%
[5 empty] | 20 /15 |  | TEFC 8 Poles | 90.2%
[7 empty] | TEFC 6 Poles | 91.7%
[7 empty] | TEFC 4 Poles | 93%
[7 empty] | TEFC 2 Poles | 91%
[5 empty] | 25/18.5 |  | TEFC 8 Poles | 90.2%
[7 empty] | TEFC 6 Poles | 93%
[7 empty] | TEFC 4 Poles | 93.6%
[7 empty] | TEFC 2 Poles | 91.7%
[5 empty] | 30 /22 |  | TEFC 8 Poles | 91.7%
[7 empty] | TEFC 6 Poles | 93%
[7 empty] | TEFC 4 Poles | 93.6%
[7 empty] | TEFC 2 Poles | 91.7%
[5 empty] | 40 /30 |  | TEFC 8 Poles | 91.7%
[7 empty] | TEFC 6 Poles | 94.1%
[7 empty] | TEFC 4 Poles | 94.1%
[7 empty] | TEFC 2 Poles | 92.4%
[5 empty] | 50 /37 |  | TEFC 8 Poles | 92.4%
[7 empty] | TEFC 6 Poles | 94.1%
[7 empty] | TEFC 4 Poles | 94.5%
[7 empty] | TEFC 2 Poles | 93%
[5 empty] | 60 /45 |  | TEFC 8 Poles | 92.4%
[7 empty] | TEFC 6 Poles | 94.5%
[7 empty] | TEFC 4 Poles | 95%
[7 empty] | TEFC 2 Poles | 93.6%
[5 empty] | 75 /55 |  | TEFC 8 Poles | 93.6%
[7 empty] | TEFC 6 Poles | 94.5%
[7 empty] | TEFC 4 Poles | 95.4%
[7 empty] | TEFC 2 Poles | 93.6%
[5 empty] | 100 /75 |  | TEFC 8 Poles | 93.6%
[7 empty] | TEFC 6 Poles | 95%
[7 empty] | TEFC 4 Poles | 95.4%
[7 empty] | TEFC 2 Poles | 94.1%
[5 empty] | 125 /90 |  | TEFC 8 Poles | 94.1%
[7 empty] | TEFC 6 Poles | 95%
[7 empty] | TEFC 4 Poles | 95.4%
[7 empty] | TEFC 2 Poles | 95%
[5 empty] | 150 /110 |  | TEFC 8 Poles | 94.1%
[7 empty] | TEFC 6 Poles | 95.8%
[7 empty] | TEFC 4 Poles | 95.8%
[7 empty] | TEFC 2 Poles | 95%
[5 empty] | 200 /150 |  | TEFC 8 Poles | 94.5%
[7 empty] | TEFC 6 Poles | 95.8%
[7 empty] | TEFC 4 Poles | 96.2%
[7 empty] | TEFC 2 Poles | 95.4%
[5 empty] | 250 /186 |  | TEFC 8 Poles | 95%
[7 empty] | TEFC 6 Poles | 95.8%
[7 empty] | TEFC 4 Poles | 96.2%
[7 empty] | TEFC 2 Poles | 95.8%
[5 empty] | 300 /224 |  | TEFC 6 Poles | 95.8%
[7 empty] | TEFC 4 Poles | 96.2%
[7 empty] | TEFC 2 Poles | 95.8%
[5 empty] | 350 /261 |  | TEFC 6 Poles | 95.8%
[7 empty] | TEFC 4 Poles | 96.2%
[7 empty] | TEFC 2 Poles | 95.8%
[5 empty] | 400 /298 |  | TEFC 4 Poles | 96.2%
[7 empty] | TEFC 2 Poles | 95.8%
[5 empty] | 450 /336 |  | TEFC 4 Poles | 96.2%
[7 empty] | TEFC 2 Poles | 95.8%
[5 empty] | 500 /373 |  | TEFC 4 Poles | 96.2%
[7 empty] | TEFC 2 Poles | 95.8%
|  |  | NEMA Design C and IEC Design H Motors at 60 Hz |  | 1/0.75 |  | ODP 8 Poles | 75.5%
[7 empty] | ODP 6 Poles | 82.5%
[7 empty] | ODP 4 Poles | 85.5%
[5 empty] | 1.5/1.1 |  | ODP 8 Poles | 77%
[7 empty] | ODP 6 Poles | 86.5%
[7 empty] | ODP 4 Poles | 86.5%
[5 empty] | 2/1.5 |  | ODP 8 Poles | 86.5%
[7 empty] | ODP 6 Poles | 87.5%
[7 empty] | ODP 4 Poles | 86.5%
[5 empty] | 3/2.2 |  | ODP 8 Poles | 87.5%
[7 empty] | ODP 6 Poles | 88.5%
[7 empty] | ODP 4 Poles | 89.5%
[5 empty] | 5/3.7 |  | ODP 8 Poles | 88.5%
[7 empty] | ODP 6 Poles | 89.5%
[7 empty] | ODP 4 Poles | 89.5%
[5 empty] | 7.5/5.5 |  | ODP 8 Poles | 89.5%
[7 empty] | ODP 6 Poles | 90.2%
[7 empty] | ODP 4 Poles | 91%
[5 empty] | 10/7.5 |  | ODP 8 Poles | 90.2%
[7 empty] | ODP 6 Poles | 91.7%
[7 empty] | ODP 4 Poles | 91.7%
[5 empty] | 15 /11 |  | ODP 8 Poles | 90.2%
[7 empty] | ODP 6 Poles | 91.7%
[7 empty] | ODP 4 Poles | 93%
[5 empty] | 20 /15 |  | ODP 8 Poles | 91%
[7 empty] | ODP 6 Poles | 92.4%
[7 empty] | ODP 4 Poles | 93%
[5 empty] | 25 /18.5 |  | ODP 8 Poles | 91%
[7 empty] | ODP 6 Poles | 93%
[7 empty] | ODP 4 Poles | 93.6%
[5 empty] | 30 /22 |  | ODP 8 Poles | 91.7%
[7 empty] | ODP 6 Poles | 93.6%
[7 empty] | ODP 4 Poles | 94.1%
[5 empty] | 40 /30 |  | ODP 8 Poles | 91.7%
[7 empty] | ODP 6 Poles | 94.1%
[7 empty] | ODP 4 Poles | 94.1%
[5 empty] | 50 /37 |  | ODP 8 Poles | 92.4%
[7 empty] | ODP 6 Poles | 94.1%
[7 empty] | ODP 4 Poles | 94.5%
[5 empty] | 60 /45 |  | ODP 8 Poles | 93%
[7 empty] | ODP 6 Poles | 94.5%
[7 empty] | ODP 4 Poles | 95%
[5 empty] | 75 /55 |  | ODP 8 Poles | 94.1%
[7 empty] | ODP 6 Poles | 94.5%
[7 empty] | ODP 4 Poles | 95%
[5 empty] | 100 /75 |  | ODP 8 Poles | 94.1%
[7 empty] | ODP 6 Poles | 95%
[7 empty] | ODP 4 Poles | 95.4%
[5 empty] | 125 /90 |  | ODP 8 Poles | 94.1%
[7 empty] | ODP 6 Poles | 95%
[7 empty] | ODP 4 Poles | 95.4%
[5 empty] | 150 /110 |  | ODP 8 Poles | 94.1%
[7 empty] | ODP 6 Poles | 95.4%
[7 empty] | ODP 4 Poles | 95.8%
[5 empty] | 200 /150 |  | ODP 8 Poles | 94.1%
[7 empty] | ODP 6 Poles | 95.4%
[7 empty] | ODP 4 Poles | 95.8%
[5 empty] | 1/0.75 |  | TEFC 8 Poles | 75.5%
[7 empty] | TEFC 6 Poles | 82.5%
[7 empty] | TEFC 4 Poles | 85.5%
[5 empty] | 1.5/1.1 |  | TEFC 8 Poles | 78.5%
[7 empty] | TEFC 6 Poles | 87.5%
[7 empty] | TEFC 4 Poles | 86.5%
[5 empty] | 2/1.5 |  | TEFC 8 Poles | 84%
[7 empty] | TEFC 6 Poles | 88.5%
[7 empty] | TEFC 4 Poles | 86.5%
[5 empty] | 3/2.2 |  | TEFC 8 Poles | 85.5%
[7 empty] | TEFC 6 Poles | 89.5%
[7 empty] | TEFC 4 Poles | 89.5%
[5 empty] | 5/3.7 |  | TEFC 8 Poles | 86.5%
[7 empty] | TEFC 6 Poles | 89.5%
[7 empty] | TEFC 4 Poles | 89.5%
[5 empty] | 7.5/5.5 |  | TEFC 8 Poles | 86.5%
[7 empty] | TEFC 6 Poles | 91%
[7 empty] | TEFC 4 Poles | 91.7%
[5 empty] | 10/7.5 |  | TEFC 8 Poles | 89.5%
[7 empty] | TEFC 6 Poles | 91%
[7 empty] | TEFC 4 Poles | 91.7%
[5 empty] | 15 /11 |  | TEFC 8 Poles | 89.5%
[7 empty] | TEFC 6 Poles | 91.7%
[7 empty] | TEFC 4 Poles | 92.4%
[5 empty] | 20 /15 |  | TEFC 8 Poles | 90.2%
[7 empty] | TEFC 6 Poles | 91.7%
[7 empty] | TEFC 4 Poles | 93%
[5 empty] | 25 /18.5 |  | TEFC 8 Poles | 90.2%
[7 empty] | TEFC 6 Poles | 93%
[7 empty] | TEFC 4 Poles | 93.6%
[5 empty] | 30 /22 |  | TEFC 8 Poles | 91.7%
[7 empty] | TEFC 6 Poles | 93%
[7 empty] | TEFC 4 Poles | 93.6%
[5 empty] | 40 /30 |  | TEFC 8 Poles | 91.7%
[7 empty] | TEFC 6 Poles | 94.1%
[7 empty] | TEFC 4 Poles | 94.1%
[5 empty] | 50 /37 |  | TEFC 8 Poles | 92.4%
[7 empty] | TEFC 6 Poles | 94.1%
[7 empty] | TEFC 4 Poles | 94.5%
[5 empty] | 60 /45 |  | TEFC 8 Poles | 92.4%
[7 empty] | TEFC 6 Poles | 94.5%
[7 empty] | TEFC 4 Poles | 95%
[5 empty] | 75 /55 |  | TEFC 8 Poles | 93.6%
[7 empty] | TEFC 6 Poles | 94.5%
[7 empty] | TEFC 4 Poles | 95.4%
[5 empty] | 100 /75 |  | TEFC 8 Poles | 93.6%
[7 empty] | TEFC 6 Poles | 95%
[7 empty] | TEFC 4 Poles | 95.4%
[5 empty] | 125 /90 |  | TEFC 8 Poles | 94.1%
[7 empty] | TEFC 6 Poles | 95%
[7 empty] | TEFC 4 Poles | 95.4%
[5 empty] | 150 /110 |  | TEFC 8 Poles | 94.1%
[7 empty] | TEFC 6 Poles | 95.8%
[7 empty] | TEFC 4 Poles | 95.8%
[5 empty] | 200 /150 |  | TEFC 8 Poles | 94.5%
[7 empty] | TEFC 6 Poles | 95.8%
[7 empty] | TEFC 4 Poles | 96.2%
| [η_EEmotor] | [7 empty] | Y |  | Efficient motor nominal/nameplate motor efficiency
| [Hours] | Building Type (HVAC) | Convenience | Motor Type | Hot Water Pump Motor |  |  | 3628 | N | Hours | Hours for HVAC motors
|  |  | Education |  |  |  |  | 3566
|  |  | Grocery |  |  |  |  | 2551
|  |  | Health |  |  |  |  | 3957
|  |  | Hospital |  |  |  |  | 4260
|  |  | Industrial |  |  |  |  | 3977
|  |  | Lodging |  |  |  |  | 5287
|  |  | Multifamily |  |  |  |  | 5287
|  |  | Office - Large |  |  |  |  | 5864
|  |  | Office - Small |  |  |  |  | 4482
|  |  | Religious |  |  |  |  | 4763
|  |  | Restaurant |  |  |  |  | 4127
|  |  | Retail - Large |  |  |  |  | 4218
|  |  | Retail - Small |  |  |  |  | 3985
|  |  | Warehouse |  |  |  |  | 4100
|  |  | Nonresidential (average) |  |  |  |  | 4253
|  |  | Convenience |  | Chilled Water Pump |  |  | 2690
|  |  | Education |  |  |  |  | 2833
|  |  | Grocery |  |  |  |  | 3994
|  |  | Health |  |  |  |  | 4369
|  |  | Hospital |  |  |  |  | 4647
|  |  | Industrial |  |  |  |  | 3080
|  |  | Lodging |  |  |  |  | 5292
|  |  | Multifamily |  |  |  |  | 5292
|  |  | Office - Large |  |  |  |  | 4608
|  |  | Office - Small |  |  |  |  | 2702
|  |  | Religious |  |  |  |  | 2223
|  |  | Restaurant |  |  |  |  | 2974
|  |  | Retail - Large |  |  |  |  | 2405
|  |  | Retail - Small |  |  |  |  | 2120
|  |  | Warehouse |  |  |  |  | 1788
|  |  | Nonresidential (average) |  |  |  |  | 3401
|  |  | Convenience |  | Fan |  |  | 4630
|  |  | Education |  |  |  |  | 1877
|  |  | Grocery |  |  |  |  | 4663
|  |  | Health |  |  |  |  | 3806
|  |  | Hospital |  |  |  |  | 6520
|  |  | Industrial |  |  |  |  | 2850
|  |  | Lodging |  |  |  |  | 3061
|  |  | Multifamily |  |  |  |  | 3061
|  |  | Office - Large |  |  |  |  | 2920
|  |  | Office - Small |  |  |  |  | 2920
|  |  | Religious |  |  |  |  | 2412
|  |  | Restaurant |  |  |  |  | 5443
|  |  | Retail - Large |  |  |  |  | 4065
|  |  | Retail - Small |  |  |  |  | 3694
|  |  | Warehouse |  |  |  |  | 2920
|  |  | Nonresidential (average) |  |  |  |  | 3656
|  | HP Range (Non-HVAC) | 1-5 |  |  |  |  | 2745 |  |  | Hours for non-HVAC motors
|  |  | 6-20 |  |  |  |  | 3391
|  |  | 21-50 |  |  |  |  | 4067
|  |  | 51-100 |  |  |  |  | 5329
|  |  | 101-200 |  |  |  |  | 5200
|  |  | 201-350 |  |  |  |  | 6132
| [CF] | [6 empty] | 79.3% | N |  | Coincidence Factor

## Forklift Battery Charger
Forklift Battery Charger
| Measure Code: | NR-MSC-BACH-V01-180101
| Lifetime of Efficient Equipment: | [7 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime | [5 empty] | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: | [7 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  |  |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
400
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = (([CAP] * [DOD]) * [CHG] * ([CRB] / [PCB] - [CREE] / [PCEE]) * [WHFe]) + [ΔkWhheatpenalty]
| Time of Sale Demand (ΔkW) | =([PFB]/[PCB] - [PFEE]/[PCEE]) * [VoltsDC] * [AmpsDC] / [1000] * [WHFd] * [CF]
| Time of Sale Gas (ΔTherms) | = ([CAP] * [DOD]) * [CHG] * ([CRB] / [PCB] -[CREE] / [PCEE]) *([- IFTherms])
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] / [HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWhheatpenalty] |  |  | =([CAP] * [DOD]) * [CHG] * ([CRB] / [PCB] - [CREE] / [PCEE]) * ([-IFkWh])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [CAP] |  |  |  |  | 35 | Y | kWh | Capacity of battery
| [DOD] |  |  |  |  | 80% | Y |  | Depth of discharge
| [CHG] | Type of Operations (Shifts) | 1-shift (8 hrs/day – 5 days/week) |  |  | 520 | Y | Number | Number of charges per year
|  |  | 2-shift (16 hrs/day – 5 days/week) |  |  | 1040
|  |  | 3-shift (24 hrs/day – 5 days/week) |  |  | 1560
|  |  | 4-shift (24 hrs/day – 7 days/week) |  |  | 2184
| [CRB] |  |  |  |  | 1.2485 | N |  | Baseline charge return factor
| [PCB] |  |  |  |  | 84% | N |  | Baseline power conversion efficiency
| [CREE] |  |  |  |  | 1.107 | N |  | Efficient charge return factor
| [PCEE] |  |  |  |  | 89% | N |  | Efficient power conversion efficiency
| [WHFe] | Building Type | Cooled Warehouse |  |  | 1.09 | N |  | Waste heat factor for demand to account for cooling savings from reduced waste heat from battery charger
|  |  | Uncooled Warehouse |  |  | 1
|  |  | Refrigerated Buildings |  |  | 1.29
| [-IFkWh] | Type of electric heating system | Electric Resistance |  |  | 0.44 | N |  | Heating Interation Factor for electric heating impacts; this factor represents the increased electric space heating requirements due to the reduction of waste heat rejected by the battery charger
|  |  | Heat Pump |  |  | 0.19
|  |  | Unheated |  |  | 0
| [PFB] |  |  |  |  | 0.9095 | N |  | Power factor of baseline charger
| [PFEE] |  |  |  |  | 0.937 | N |  | Power factor of high frequency charger
| [VoltsDC] |  |  |  |  | 48 | Y | Volts | Actual DC rated voltage of charger (assumed baseline charger is replaced with same rated high frequency unit)
| [AmpsDC] |  |  |  |  | 81 | Y | Amps | Actual DC rated amperage of charger (assumed baseline charger is replaced with same rated high frequency unit)
| [1000] |  |  |  |  | 1000 | N | W to kW | Watt to kilowatt conversion factor
| [WHFd] | Building Type | Cooled Warehouse |  |  | 1.43 | N |  | Waste heat factor for demand to account for cooling energy savings from reduced waste heat from the battery charger
|  |  | Uncooled Warehouse |  |  | 1
|  |  | Refrigerated Buildings |  |  | 1.29
| [CF] | Type of Operations (Shifts) | 1 and 2-shift |  |  | 0 | N |  | Summer Coincident Peak Factor
|  |  | 3 and 4-shift |  |  | 1
| [IFTherms] | Gas heated? | Gas heated |  |  | 0.019 | N |  | Heating Interation Factor for gas heating impacts; this factor represents the increased gas space heating requirements due to the reduction of waste heat rejected by the battery charger
|  |  | Unheated |  |  | 0
| [ΔTherms] | [5 empty] | C | therms | Therm impact calcuated above
| [HeatDays] |  |  |  |  | 197 | N |  | Heat season days per year

## Dishwasher
Dishwasher
| Measure Code: | NR-FSE-DISH-V02-190101
| Lifetime of Efficient Equipment: | [6 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
| Dishwasher Type | Under Counter | Temperature | Low | 10
|  | Stationary Single Tank Door |  |  | 15
|  | Single Tank Conveyor |  |  | 20
|  | Multi Tank Conveyor |  |  | 20
|  | Under Counter |  | High | 10
|  | Stationary Single Tank Door |  |  | 15
|  | Single Tank Conveyor |  |  | 20
|  | Multi Tank Conveyor |  |  | 20
|  | Pot, Pan, Utensil |  |  | 10
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Dishwasher Type | Under Counter | Temperature | Low | 50
|  | Stationary Single Tank Door |  |  | 0
|  | Single Tank Conveyor |  |  | 0
|  | Multi Tank Conveyor |  |  | 970
|  | Under Counter |  | High | 120
|  | Stationary Single Tank Door |  |  | 770
|  | Single Tank Conveyor |  |  | 2050
|  | Multi Tank Conveyor |  |  | 970
|  | Pot, Pan, Utensil |  |  | 1710
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =[∆BuildingEnergy] + [∆BoosterEnergy] + [∆IdleEnergy]
| Time of Sale Demand (ΔkW) | =[∆kWh] / ([Hours] * [Days]) * [CF]
| Time of Sale Gas (ΔTherms) | =[ ∆BuildingEnergy] + [∆BoosterEnergy]
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] / [Days]
| Time of Sale Water (ΔGallons) | =([WaterUse_Base] * [RacksWashed] * [Days])- ([WaterUse_ESTAR] * [RacksWashed] * [Days])
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [∆BuildingEnergy] | Building Water Heater Fuel | Electric | = [([WaterUseBase] * [RacksWashed] * [Days]) * ([∆Tin] * [1.0] * [8.2] / [EffHeaterElec] / [3,412])] - [([WaterUseESTAR] * [RacksWashed] * [Days]) * ([∆Tin] * [1.0] * [8.2] / [EffHeaterElec] / [3,412])]
|  |  | Gas | = [([WaterUseBase] * [RacksWashed] * [Days]) * ([∆Tin] * [1.0] * [8.2] / [EffHeaterGas] / [100000])] - [([WaterUseESTAR] * [RacksWashed] * [Days]) * ([∆Tin] * [1.0] * [8.2] / [EffHeaterGas] / [100000])]
| [∆BoosterEnergy] | Booster Water Heater Fuel | Electric | = [([WaterUseBase] * [RacksWashed] * [Days]) * ([∆Tin] * [1.0] * [8.2] / [EffHeaterElec] / [3,412])] - [([WaterUseESTAR] * [RacksWashed] * [Days]) * ([∆Tin] *[1.0] * [8.2] / [EffHeaterElec] / [3,412])]
|  |  | Gas | = [([WaterUseBase] * [RacksWashed] * [Days]) * ([∆Tin] * [1.0] * [8.2] / [EffHeaterGas] / [100000])] - [([WaterUseESTAR] * [RacksWashed] * [Days]) * ([∆Tin] *[1.0] * [8.2] / [EffHeaterGas] / [100000])]
| [∆IdleEnergy] |  |  | = [[IdleDrawBase] * ([Hours] * [Days] – [Days] * [RacksWashed] * [WashTime] / [60])] – [[IdleDrawESTAR] * ([Hours] * [Days] – [Days] * [RacksWashed] * [WashTime] / [60])]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [ΔBuildingEnergy] | [5 empty] | C |  | Change in annual energy consumption of building water heater
| [ΔBoosterEnergy] | [5 empty] | C |  | Annual energy consumption of booster water heater
| [ΔIdleEnergy] | [5 empty] | C |  | Annual idle electric energy consumption of dishwasher
| [WaterUseBase] | Temperature | Low | Dishwasher Type | Under Counter | 1.73 | Y | gallons | Water use per rack (gal) of baseline dishwasher
[5 empty] | Stationary Single Tank Door | 2.1
[5 empty] | Single Tank Conveyor | 1.31
[5 empty] | Multi Tank Conveyor | 1.04
|  |  | High |  | Under Counter | 1.09
[5 empty] | Stationary Single Tank Door | 1.29
[5 empty] | Single Tank Conveyor | 0.87
[5 empty] | Multi Tank Conveyor | 0.97
[5 empty] | Pot, Pan, Utensil | 0.7
| [WaterUseESTAR] | Temperature | Low | Dishwasher Type | Under Counter | 1.19 | Y | gallons | Water use per rack (gal) of ENERGY STAR dishwasher
[5 empty] | Stationary Single Tank Door | 1.18
[5 empty] | Single Tank Conveyor | 0.79
[5 empty] | Multi Tank Conveyor | 0.54
|  |  | High |  | Under Counter | 0.86
[5 empty] | Stationary Single Tank Door | 0.89
[5 empty] | Single Tank Conveyor | 0.7
[5 empty] | Multi Tank Conveyor | 0.54
[5 empty] | Pot, Pan, Utensil | 0.58
| [RacksWashed] | Temperature | Low | Dishwasher Type | Under Counter | 75 | Y |  | Number of racks washed per day
[5 empty] | Stationary Single Tank Door | 280
[5 empty] | Single Tank Conveyor | 400
[5 empty] | Multi Tank Conveyor | 600
|  |  | High |  | Under Counter | 75
[5 empty] | Stationary Single Tank Door | 280
[5 empty] | Single Tank Conveyor | 400
[5 empty] | Multi Tank Conveyor | 600
[5 empty] | Pot, Pan, Utensil | 280
| [Days] |  |  |  |  | 365.25 | Y | Days | Annual days of dishwasher operation
| [ΔTin] | Building water heaters |  |  |  | 83.5 | Y | °F | Inlet water temperature increase (°F)
|  | Booster water heaters |  |  |  | 40
| [1.0] |  |  |  |  | 1 | N | Btu/lb/°F | Specific heat of water
| [8.2] |  |  |  |  | 8.2 | N | lb/gal | Density of water
| [EffHeaterElec] |  |  |  |  | 98% | Y |  | Efficiency of water heater for electric building and booster water heaters
| [3412] |  |  |  |  | 3412 | N | kWh to Btu | kWh to Btu conversion factor
| [IdleDrawBase] | Temperature | Low | Dishwasher Type | Under Counter | 0.5 | Y |  | Idle power draw (kW) of baseline dishwasher
[5 empty] | Stationary Single Tank Door | 0.6
[5 empty] | Single Tank Conveyor | 1.6
[5 empty] | Multi Tank Conveyor | 2
|  |  | High |  | Under Counter | 0.76
[5 empty] | Stationary Single Tank Door | 0.87
[5 empty] | Single Tank Conveyor | 1.93
[5 empty] | Multi Tank Conveyor | 2.59
[5 empty] | Pot, Pan, Utensil | 1.2
| [IdleDrawESTAR] | Temperature | Low | Dishwasher Type | Under Counter | 0.5 | Y |  | Idle power draw (kW) of ENERGY STAR dishwasher
[5 empty] | Stationary Single Tank Door | 0.6
[5 empty] | Single Tank Conveyor | 1.5
[5 empty] | Multi Tank Conveyor | 2
|  |  | High |  | Under Counter | 0.5
[5 empty] | Stationary Single Tank Door | 0.7
[5 empty] | Single Tank Conveyor | 1.5
[5 empty] | Multi Tank Conveyor | 2.25
[5 empty] | Pot, Pan, Utensil | 1.2
| [Hours] |  |  |  |  | 18 | Y | Hours | Average daily hours of diswasher operation
| [WashTime] | Temperature | Low | Dishwasher Type | Under Counter | 2 | Y | Minutes | Typical wash time
[5 empty] | Stationary Single Tank Door | 1.5
[5 empty] | Single Tank Conveyor | 0.3
[5 empty] | Multi Tank Conveyor | 0.3
|  |  | High |  | Under Counter | 2
[5 empty] | Stationary Single Tank Door | 1
[5 empty] | Single Tank Conveyor | 0.3
[5 empty] | Multi Tank Conveyor | 0.2
[5 empty] | Pot, Pan, Utensil | 3
| [60] |  |  |  |  | 60 | N | Minutes | Minutes to hours conversion factor
| [ΔkWh] | [5 empty] | C | kWh | Electric energy savings, calculated above
| [CF] |  |  |  |  | 0.638 | N |  | Summer peak coincidence factor
| [EffHeaterGas] | Building water heaters |  |  |  | 78% | Y |  | Efficiency for gas building and booster water heaters
|  | Booster water heaters |  |  |  | 80%
| [100,000] |  |  |  |  | 100000 | N | therms to btu | Therms to Btu conversion factor
| [Δtherms] | [5 empty] | C | therms | Natural gas energy savings

## Com Solid and Glass Door Fridge
Com Solid and Glass Door Fridge
| Measure Code: | NR-FSE-CSGD-V01-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
12
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Equipment Type | Solid Door Refrigerator | $24.21 per cu. ft.
|  | Glass Door Refrigerator | $24.77 per cu. ft.
|  | Solid Door Freezer | $30.41 per cu. ft.
|  | Glass Door Freezer | $33.01 per cu. ft.
|  | Solid or Glass Door Chest Refrigerator | $57.11 per cu. ft.
|  | Solid or Glass Door Chest Freezerr | $75.90 per cu. ft.
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([kWh_Base] - [kWh_ESTAR] )* [Days]
| Time of Sale Demand (ΔkW) | =([∆kWh] / [HOURS]) * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Sub Algorithm
| [kWhBase] | Equipment Type | Solid Door Refrigerator |  |  | 0.05V + 1.36
|  |  | Glass Door Refrigerator |  |  | 0.1V + 0.86
|  |  | Solid Door Freezer |  |  | 0.22V + 1.38
|  |  | Glass Door Freezer |  |  | 0.29V + 2.95
|  |  | Solid Door Chest Refrigerator |  |  | 0.05V + 0.91
|  |  | Glass Door Chest Refrigerator |  |  | 0.06V + 0.37
|  |  | Solid Door Chest Freezer |  |  | 0.06V + 1.12
|  |  | Glass Door Chest Freezer |  |  | 0.08V + 1.23
| [kWhESTAR] | Equipment Type | Vertical Closed Solid Door Refrigerator | Volume (Ft3) | 0 < V < 15 | ≤ 0.022V + 0.97
[5 empty] | 15 ≤ V < 30 | ≤ 0.066V + 0.31
[5 empty] | 30 ≤ V < 50 | ≤ 0.04V + 1.09
[5 empty] | V ≥ 50 | ≤ 0.024V + 1.89
|  |  | Vertical Closed Glass Door Refrigerator |  | 0 < V < 15 | ≤ 0.095V + 0.445
[5 empty] | 15 ≤ V < 30 | ≤ 0.05V + 1.12
[5 empty] | 30 ≤ V < 50 | ≤ 0.076V + 0.34
[5 empty] | V ≥ 50 | ≤ 0.105V + 1.111
|  |  | Horizontal Closed Solid or Glass Doors Refrigerator |  | All volumes | ≤ 0.05V + 0.28
|  |  | Vertical Closed Solid Door Freezer |  | 0 < V < 15 | ≤ 0.21V + 0.90
[5 empty] | 15 ≤ V < 30 | ≤ 0.12V + 2.248
[5 empty] | 30 ≤ V < 50 | ≤ 0.285V - 2.703
[5 empty] | V ≥ 50 | ≤ 0.142V + 4.445
|  |  | Vertical Closed Glass Door Freezer |  | All volumes | ≤ 0.232V + 2.36
|  |  | Horizontal Closed Solid or Glass Doors Freezer |  | All volumes | ≤ 0.057V + 0.55
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [kWhBase] | [5 empty] | C | kWh | Maximum daily energy consumption (kWh/day) of baseline refrigerator or freezer
| [kWhESTAR] | [5 empty] | C | kWh | Maximum daily energy consumption (kWh/day) of ENERGY STAR refrigerator or freezer
| [V] | [5 empty] | Y | ft3 | Refrigerated volume (ft3) calculated in accordance with the Department of Energy test procedure in 10 CFR §431.64
| [Days] |  |  |  |  | 365.25 | N | Days | Days of refrigerator or freezer operations per year
| [ΔkWh] | [5 empty] | C | kWh | Electric energy savings, calculated above
| [Hours] |  |  |  |  | 8766 | N | Hours | Hours of refrigerator or freezer operation per year
| [CF] |  |  |  |  | 0.964 | N |  | Summer peak coincidence factor

## Pre-Rinse Spray Valve
Pre-Rinse Spray Valve
| Measure Code: | NR-FSE-SPRY-V03-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
5
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Program Type / Replacement Scenario | Time of Sale (TOS) | 0
|  | Direct Install (DI) | 54
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [HotPercentage] * ([T_out]-[T_in]) * [1.0] * [8.33] / [Eff_Heater] / [3,412] *[∆WaterUse]
| Time of Sale Demand (ΔkW) | =[∆kWh] / (([Minutes] / [60)*[Days]) * [CF]
| Time of Sale Gas (ΔTherms) | = [HotPercentage] * ([T_out]-[T_in]) * [1.0] * [8.33] / [Eff_Heater] / [100000] *[∆WaterUse]
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] / [Days]
| Time of Sale Water (ΔGallons) | =([Flow_Base] - [Flow_EE] ) * [Minutes] * [Days]
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [ΔkWh] | Program Type | TOS |  |  | 1215.6 | C | kWh | Deemed value or use algorithm
|  |  | DI |  |  | 5640.6
| [HotPercentage] |  |  |  |  | 100% | Y |  | Percentage of hot water used for rinse
| [Tout] |  |  |  |  | 140 | Y | °F | Unmixed Outlet Water Temperature from the DHW system
| [Tin] |  |  |  |  | 56.5 | Y | °F | Inlet Water Temperature to the DHW system
| [1.0] |  |  |  |  | 1 | N | Btu/lb/°F | Specific heat of water
| [8.33] |  |  |  |  | 8.33 | N | lb/gal | Specific weight capacity of water
| [EffHeaterElec] |  |  |  |  | 98% | Y |  | Efficiency of electric water heater
| [3412] |  |  |  |  | 3412 | N | kWh to Btu | kWh to Btu conversion factor
| [ΔWaterUse] | TOS |  |  |  | 5844 | C | gal/yr | Change in annual water consumption, Custom calculation in Water Impact Descriptions and Calculation section of this measure, otherwise use 7,480.3 gal/yr for TOS and 22,207.2 gal/yr for DI
|  | DI |  |  |  | 27116
| [Minutes] |  |  |  |  | 64 | Y | minutes | Average daily minutes of spray valve operation
| [60] |  |  |  |  | 60 | N | minutes | Minutes to hours conversion factor
| [Days] |  |  |  |  | 365.25 | Y | days | Annual days of operation
| [CF] | Restaurant Type | Fast-food |  |  | 0.0114 | N |  | Summer peak coincidence factor
|  |  | Sit-down |  |  | 0.025
| [Δtherms] | Program Type | TOS |  |  | 52.1 | C | Therms | Deemed value or use algorithm
|  |  | DI |  |  | 241.8
| [EffHeaterGas] |  |  |  |  | 78% | Y |  | Efficiency for gas water heaters
| [100,000] |  |  |  |  | 100000 | N | therms to btu | Therms to Btu conversion factor
| [FlowBase] | TOS |  |  |  | 1.23 | Y | gal/min | Flow rate (gal/min) of baseline pre-rinse spray valve
|  | DI |  |  |  | 2.14
| [FlowEE] |  |  |  |  | 0.98 | Y | gal/min | Flow rate (gal/min) of efficient pre-rinse spray valve

## Infrared Upright Broiler
Infrared Upright Broiler
| Measure Code: | NR-FSE-IRUB-V01-170101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
10
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
5900
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | =(([InputRate_Base] - [InputRate_EE]) * ([Duty] * [Hours]) / [100,000])
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] / [Days]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Δtherms] | [5 empty] | C | therms | Use algorithm or assume deemed factor of 2.7 therms / Mbtu/hr
| [InputRateBase] |  |  |  |  | 95000 | N | Btu/hr | Rated energy input rate of baseline upright broiler (Btu/hr)
| [InputRateEE] |  |  |  |  | 82333 | Y | Btu/hr | Rated energy input rate of infrared upright broiler (Btu/hr)
| [Duty] |  |  |  |  | 70% | Y |  | Duty cycle of upright boiler
| [Hours] |  |  |  |  | 2496 | Y | hours | Typical operating hours of upright boiler
| [100000] |  |  |  |  | 100000 | N | Btu to therms | Btu to therms conversion factor
| [Days] |  |  |  |  | 312 | C | days | Custom or if unknown, use 312 days per year

## Infrared Salamander Broiler
Infrared Salamander Broiler
| Measure Code: | NR-FSE-IRBL-V01-170101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
12
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
1000
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | =(([InputRate_Base] - [InputRate_EE]) * ([Duty] * [Hours]) / [100,000])
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [ Δtherms] | [5 empty] | C | therms | Use algorithm or assume deemed factor of 9.7 therms / Mbtu/hr
| [InputRateBase] |  |  |  |  | 38500 | N | Btu/hr | Rated energy input rate of baseline salamander broiler (Btu/hr)
| [InputRateEE] |  |  |  |  | 24750 | Y | Btu/hr | Rated energy input rate of infrared salamander broiler (Btu/hr)
| [Duty] |  |  |  |  | 70% | Y |  | Duty cycle of salamander boiler
| [Hours] |  |  |  |  | 2496 | Y | hours | Typical operating hours of salamander boiler
| [100000] |  |  |  |  | 100000 | N | Btu to therms | Btu to therms conversion factor
| [Days] |  |  |  |  | 312 | C | days | Custom or if unknown, use 312 days per year

## Infrared Charbroiler
Infrared Charbroiler
| Measure Code: | NR-FSE-IRCB-V01-170101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
12
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
2200
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | =[([∆PreheatEnergy] + [∆CookingEnergy]) * [Days] / [100,000]] /
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] / [Days]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔPreheatEnergy] |  |  | = ([PreheatRateBase] * [Preheats] * [PreheatTime] / [60]) - ([PreheatRateEE] * [Preheats] * [PreheatTime] / [60])
| [ΔCookingEnergy] |  |  | = ([InputRateBase] - [InputRateEE]) * [Hours]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Δtherms] | [5 empty] | C | therms | Use algorithm or assume deemed factor of 8.4 therms / Mbtu/hr
| [Days] |  |  |  |  | 312 | Y | days | Custom or if unknown, use 312 days per year
| [100000] |  |  |  |  | 100000 | N | Btu to therms | Btu to therms conversion factor
| [PreheatRateBase] |  |  |  |  | 64000 | N | Btu/hr | Preheat energy rate of baseline charbroiler
| [PreheatRateEE] |  |  |  |  | 54000 | Y | Btu/hr | Preheat energy rate of infrared charbroiler
| [Preheats] |  |  |  |  | 1 | Y |  | Number of preheats per day
| [PreheatTime] |  |  |  |  | 15 | Y | minutes | Length of one preheat
| [60] |  |  |  |  | 60 | N | minutes to hour | Minutes to hours conversion factor
| [InputRateBase] |  |  |  |  | 128000 | N | Btu/hr | Input energy rate of baseline charbroiler
| [InputRateEE] |  |  |  |  | 96000 | Y | Btu/hr | Input energy rate of infrared charbroiler
| [Hours] |  |  |  |  | 8 | Y | hours | Average daily hours of operation

## Convection Oven
Convection Oven
| Measure Code: | NR-FSE-ESCV-V01-170101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
12
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
400
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([∆IdleEnergy] + [∆CookingEnergy]) * [Days] / [1,000]
| Time of Sale Demand (ΔkW) | =[∆kWh] / ([Hours] * [Days]) * [CF]
| Time of Sale Gas (ΔTherms) | =([∆IdleEnergy] + [∆CookingEnergy]) * [Days] / [100,000]
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] / [Days]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔIdleEnergy ] | Oven Fuel | Electric | = ([IdleRateBaseElec] * ([Hours] - [FoodCooked] / [ProductionBaseElec])) - ([IdleRateESTARElec] * ([Hours] - [FoodCooked] / [ProductionESTARElec]))
|  |  | Gas | = ([IdleRateBaseGas] * ([Hours] - [FoodCooked] / [ProductionBaseGas])) - ([IdleRateESTARGas] * ([Hours] - [FoodCooked] / [ProductionESTARGas]))
| [ΔCookingEnergy] | Oven Fuel | Electric | = ([FoodCooked] * [EFOODElec] / [EffBaseElec]) - ([FoodCooked] * [EFOODElec] / [EffESTARElec])
| [ΔCookingEnergy] |  | Gas | = ([FoodCooked] * [EFOODGas] / [EffBaseGas]) - ([FoodCooked] * [EFOODGas] / [EffESTARGas])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [ΔkWh] | Oven size | Full |  |  | 1938.5 | C | kWh | Deemed value or use algorithm
|  |  | Half |  |  | 192.1
| [Hours] |  |  |  |  | 12 | Y | hours | Average daily hours of operation
| [Days] |  |  |  |  | 365.25 | Y | days | Annual days of operation
| [1000] |  |  |  |  | 1000 | N | Wh to kWh | Wh to kWh conversion factor
| [FoodCooked] |  |  |  |  | 100 | Y | lbs | Food cooked per day
| [ProductionBaseElec] | Oven size | Full |  |  | 90 | N | lb/hr | Production capacity of baseline electric convection oven
|  |  | Half |  |  | 45
| [ProductionESTARElec] | Oven size | Full |  |  | 90 | Y | lb/hr | Production capacity of ENERGY STAR electric convection oven
|  |  | Half |  |  | 50
| [IdleRateBaseElec] | Oven size | Full |  |  | 2000 | N | W | Idle energy rate of baseline electric convection oven
|  |  | Half |  |  | 1030
| [IdleRateESTARElec] | Oven size | Full |  |  | 1600 | Y | W | Idle energy rate of ENERGY STAR electric convection oven
|  |  | Half |  |  | 1000
| [EFOODElec] |  |  |  |  | 73.2 | N | Wh/lb | ASTM energy to food
| [EffBaseElec] | Oven size | Full |  |  | 65% | N |  | Cooking efficiency of baseline electric convection oven
|  |  | Half |  |  | 68%
| [EffESTARElec] | Oven size | Full |  |  | 71% | Y |  | Cooking efficiency of ENERGY STAR electric convection oven
Half
| [CF] |  |  |  |  | 0.787 | N |  | Summer peak coincidence factor
| [100,000] |  |  |  |  | 100000 | N | Btu to therms | Btu to therms conversion factor
| [ProductionBaseGas] |  |  |  |  | 83 | N | lb/hr | Production capacity of baseline gas convection oven
| [ProductionESTARGas] |  |  |  |  | 86 | N | lb/hr | Production capacity of ENERGY STAR gas convection oven
| [IdleRateBaseGas] |  |  |  |  | 15100 | N | Btu/hr | Idle energy rate of baseline gas convection oven
| [IdleRateESTARGas] |  |  |  |  | 12000 | Y | Btu/hr | Idle energy rate of ENERGY STAR gas convection oven
| [EFOODGas] |  |  |  |  | 252 | N | Btu/lb | ASTM energy to food
| [EffBaseGas] |  |  |  |  | 44% | N |  | Cooking efficiency of baseline gas convection oven
| [EffESTARGas] |  |  |  |  | 46% | Y |  | Cooking efficiency of ENERGY STAR gas convection oven
| [Δtherms] | [5 empty] | C |  | Natural gas energy savings calcuated above

## Conveyor Oven
Conveyor Oven
| Measure Code: | NR-FSE-CVOV-V03-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
12
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
1800
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | =([∆PreheatEnergy] + [∆IdleEnergy] + [∆CookingEnergy]) *[ Days] / [100,000]
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] / [Days]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔPreheatEnergy] |  |  | = ([PreheatEnergyBase] * [Preheats]) - ([PreheatEnergyEE] * [Preheats])
| [ΔIdleEnergy] |  |  | = [IdleRateBase] * ([Hours] – ([FoodCooked] / [ProductionBase]) – ([Preheats] * [PreheatTime] / [60])) - [IdleRateEE] * ([Hours] – ([FoodCooked] / [ProductionEE]) – ([Preheats] * [PreheatTime] / [60]))
| [ΔCookingEnergy] |  |  | = ([FoodCooked] * [EFOOD] / [EffBase]) - ([FoodCooked] * [EFOOD] / [EffEE])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Days] |  |  |  |  | 312 | Y | Days | Annual days of operation
| [100,000] |  |  |  |  | 10000 | N | Btu to therms | Btu to therms conversion factor
| [PreheatEnergyBase] |  |  |  |  | 35000 | N | Btu | Preheat energy of baseline oven
| [PreheatEnergyEE] |  |  |  |  | 18000 | Y | Btu | Preheat energy of efficient oven
| [Preheats] |  |  |  |  | 1 | Y |  | Number of preheats per day
| [60] |  |  |  |  | 60 | N | Minutes to hours | Minutes to hours conversion factor
| [IdleRateBase] |  |  |  |  | 70000 | N | Btu/hr | Idle energy rate of baseline oven
| [IdleRateEE] |  |  |  |  | 57000 | Y | Btu/hr | Idle energy rate of efficient oven
| [Hours] |  |  |  |  | 10 | Y | Hours | Average daily hours of operation
| [FoodCooked] |  |  |  |  | 250 | Y | Pizzas | Number of pizzas cooked per day
| [ProductionBase] |  |  |  |  | 150 | N | Pizza/hr | Production capacity of baseline oven
| [ProductionEE ] |  |  |  |  | 220 | Y | Pizza/hr | Production capacity of efficient oven
| [EFOOD] |  |  |  |  | 170 | N | Btu/pizza | ASTM energy for food
| [EffBase] |  |  |  |  | 20% | N |  | Cooking efficiency of baseline oven
| [EffEE] |  |  |  |  | 42% | Y |  | Cooking efficiency of efficient oven
| [Δtherms] | [5 empty] | C |  | Natural gas energy savings calcuated above
| [Days] |  |  |  |  | 312 | Y | days | Annual days of operation

## Infrared Rotisserie Oven
Infrared Rotisserie Oven
| Measure Code: | NR-FSE-IROV-V01-170101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
12
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
2700
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh)
Time of Sale Demand (ΔkW)
| Time of Sale Gas (ΔTherms) | =(([InputRate_Base] - [InputRate_EE]) * ([Duty] * [Hours]) / [100,000])
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] / [Days]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [InputRateBase] |  |  |  |  | 50000 | N | Btu/hr | Energy input rate of baseline rotisserie oven (Btu/hr)
| [InputRateEE] |  |  |  |  | 40323 | Y | Btu/hr | Energy input rate of infrared rotisserie oven (Btu/hr)
| [Duty] |  |  |  |  | 60% | N |  | Duty cycle of rotisserie oven (%)
| [Hours] |  |  |  |  | 2496 | Y | Hours | Typical operating hours of rotisserie oven
| [100000] |  |  |  |  | 100000 | N | Btu to therms | Btu to therms conversion factor
| [1000] |  |  |  |  | 1000 | N | Btu to Mbtu | Btu to Mbtu conversion factor
| [Δtherms] | [5 empty] | C |  | Natural gas energy savings calcuated above. Use algorithm or deemed value of 3.6 therms/Mbtu/hr input.
| [Days] |  |  |  |  | 312 | Y | days | Annual days of operation

## Commercial Steam Cooker
Commercial Steam Cooker
| Measure Code: | NR-FSE-STMC-V02-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
12
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Fuel Type | Electric |  |  | 3400
|  | Natural Gas |  |  | 2270
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =[(∆IdleEnergy] + [ ∆CookingEnergy]) * [Days] / [1,000]
| Time of Sale Demand (ΔkW) | =[∆kWh] / ([Hours] * [Days]) * [CF]
| Time of Sale Gas (ΔTherms) | =([∆IdleEnergy] + [∆CookingEnergy]) * [Days] / [100,000]
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] / [Days]
| Time of Sale Water (ΔGallons) | =([∆WaterUse_Base] - [∆WaterUse_ESTAR]) * [Hours] * [Days]
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔIdleEnergy] | Cooker Fuel | Electric | = [((1 – [SteamMode]) * [IdleRateBaseElec] + [SteamMode] * [ProductionBaseElec] * [Pans] * [EFOODElec] / [EffBaseElec]) * ([Hours] – [FoodCooked] / [ProductionBaseElec] * [Pans])) - [((1 – [SteamMode] * [IdleRateESTARElec] + [SteamMode] * [ProductionESTARElec] * [Pans] * [EFOODElec] / [EffESTARElec]) * ([Hours] – [FoodCooked] / [ProductionESTARElec] * [Pans]))
|  |  | Gas | = [((1 – [SteamMode]) * ([IdleRateBaseGas] + [SteamMode] * [ProductionBaseGas] * [Pans] * [EFOODGas] / [EffBaseGas]) * ([Hours] – [FoodCooked] / [ProductionBaseGas] * [Pans])] - [(1 – [SteamMode]) * ([IdleRateESTARGas] + [SteamMode] * [ProductionESTARGas] * [Pans] * [EFOODGas] / [EffESTARGas]) * ([Hours] – [FoodCooked] / [ProductionESTARGas] * [Pans])]
| [ΔCookingEnergy] | Cooker Fuel | Electric | = ([FoodCooked] * [EFOODElec] / [EffBaseElec]) - ([FoodCooked] * [EFOODElec] / [EffESTARElec])
|  |  | Gas | = ([FoodCooked] * [EFOODGas] / [EffBaseGas]) - ([FoodCooked] * [EFOODGas] / [EffESTARGas])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Days] |  |  |  |  | 365.25 | Y | Days | Annual days of operation
| [1000] |  |  |  |  | 1000 | N | Wh to kWh | Wh to kWh conversion factor
| [SteamMode] |  |  |  |  | 40% | Y |  | Time (%) in constant steam mode
| [IdleRateBaseElec] | Pan Capacity | 3 |  |  | 1100 | N | W | Idle energy rate (W) of baseline electric steam cooker
4
5
6
10
| [IdleRateESTARElec] | Pan Capacity | 3 |  |  | 400 | Y | W | Idle energy rate (W) of ENERGY STAR electric steam cooker
|  |  | 4 |  |  | 530
|  |  | 5 |  |  | 670
|  |  | 6 |  |  | 800
|  |  | 10 |  |  | 800
| [ProductionBaseElec] |  |  |  |  | 23.3 | N | lb/hr | Production capacity (lb/hr) per pan of baseline electric steam cooker
| [ProductionESTARElec] |  |  |  |  | 16.7 | Y | lb/hr | Production capacity (lb/hr) per pan of ENERGY STAR electric steam cooker
| [Pans] |  |  |  |  | 6 | Y |  | Number of pans per steam cooker
| [EFOODElec] |  |  |  |  | 30.8 | N | Wh/lb | ASTM energy to food
| [EffBaseElec] |  |  |  |  | 28% | N |  | Cooking efficiency (%) of baseline electric steam cooker
| [EffESTARElec] |  |  |  |  | 50% | Y |  | Cooking efficiency (%) of ENERGY STAR electric steam cooker
| [Hours] |  |  |  |  | 12 | Y | Hours | Average daily hours of opertion
| [FoodCooked] |  |  |  |  | 100 | Y | lbs | Food cooked per day (lbs)
| [ΔkWh] | Pan Capacity | 3 |  |  | 10801.3 | C | kWh | Electric energy savings, calculated above. Deemed values provided.
|  |  | 4 |  |  | 13234.5
|  |  | 5 |  |  | 15609.9
|  |  | 6 |  |  | 17991.6
|  |  | 10 |  |  | 28750.1
|  |  | Average |  |  | 17277.5
| [CF] |  |  |  |  | 0.787 | N |  | Summer peak coincidence factor
| [100000] |  |  |  |  | 100000 | N | Btu to therms | Btu to therms conversion factor
| [IdleRateBaseGas] | Pan Capacity | 3 |  |  | 165000 | N | Btu/hr | Idle energy rate (W) of baseline gas steam cooker
5
6
10
| [IdleRateESTARGas] | Pan Capacity | 3 |  |  | 6250 | N | Btu/hr | Idle energy rate (W) of ENERGY STAR gas steam cooker
|  |  | 5 |  |  | 10400
|  |  | 6 |  |  | 12500
|  |  | 10 |  |  | 12500
| [ProductionBaseGas] |  |  |  |  | 23.3 | N | lb/hr | Production capacity (lb/hr) per pan of baseline gas steam cooker
| [ProductionESTARGas] |  |  |  |  | 20 | Y | lb/hr | Production capacity (lb/hr) per pan of ENERGY STAR gas steam cooker
| [EFOODGas] |  |  |  |  | 105 | N | Btu/lb | ASTM energy to food
| [EffBaseGas] |  |  |  |  | 16.5% | N |  | Cooking efficiency (%) of baseline gas steam cooker
| [EffESTARGas] |  |  |  |  | 38% | Y |  | Cooking efficiency (%) of ENERGY STAR gas steam cooker
| [Δtherms] | Pan Capacity | 3 |  |  | 808.7 | C | Therms | Natural gas energy savings calcuated above. Deemed values provided.
|  |  | 5 |  |  | 1046.4
|  |  | 6 |  |  | 1159.4
|  |  | 10 |  |  | 1812.9
|  |  | Average |  |  | 1150
| [WaterUseBase] |  |  |  |  | 40 | N | gal/hr | Water use (gal/hr) of baseline steam cooker
| [WaterUseESTAR] |  |  |  |  | 9.3 | Y | gal/hr | Water use (gal/hr) of ENERGY STAR steam cooker

## Fryer
Fryer
| Measure Code: | NR-FSE-ESFR-V02-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
12
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Fuel Type | Electric | Size | Standard | 276
|  |  |  | Large Vat | 1150
|  | Gas |  | Standard | 1860
|  |  |  | Large Vat | 1850
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([∆IdleEnergy] + [∆CookingEnergy]) * [Days] / [1,000]
| Time of Sale Demand (ΔkW) | =[∆kWh] / ([Hours] * [Days]) * [CF]
| Time of Sale Gas (ΔTherms) | =([∆IdleEnergy] + [∆CookingEnergy]) * [Days] / [100,000]
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] / [Days]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔIdleEnergy] | Cooker Fuel | Electric | = ([IdleRateBaseElec] * ([Hours] - [FoodCooked] / [ProductionBaseElec])) - ([IdleRateESTARElec] * ([Hours] - [FoodCooked] / [ProductionESTARElec]))
|  |  | Gas | = ([IdleRateBaseGas] * ([Hours] - [FoodCooked] / [ProductionBaseGas])) - ([IdleRateESTARGas] * ([Hours] - [FoodCooked] / [ProductionESTARGas]))
| [ΔCookingEnergy] | Cooker Fuel | Electric | = ([FoodCooked] * [EFOODElec] / [EffBaseElec]) - ([FoodCooked] * [EFOODElec] / [EffESTARElec])
|  |  | Gas | = ([FoodCooked] * [EFOODGas] / [EffBaseGas]) - ([FoodCooked] * [EFOODGas] / [EffESTARGas])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Hours] | Fryer Size | Standard Vat |  |  | 16 | Y | Hours | Average daily hours of operation
|  |  | Large Vat |  |  | 12
| [Days] |  |  |  |  | 365.25 | Y | Days | Annual days of operation
| [1,000] |  |  |  |  | 1000 | N | Wh to kWh | Wh to kWh conversion factor
| [FoodCooked] |  |  |  |  | 150 | Y | lbs | Food cooked per day
| [ProductionBaseElec] | Fryer Size | Standard Vat |  |  | 65 | N | lb/hr | Production capacity of baseline electric fryer
|  |  | Large Vat |  |  | 100
| [ProductionESTARElec] | Fryer Size | Standard Vat |  |  | 70 | Y | lb/hr | Production capacity of ENERGY STAR electric fryer
|  |  | Large Vat |  |  | 110
| [IdleRateBaseElec] | Fryer Size | Standard Vat |  |  | 1200 | N | W | Idle energy rate of baseline electric fryer
|  |  | Large Vat |  |  | 1350
| [IdleRateESTARElec] | Fryer Size | Standard Vat |  |  | 800 | Y | W | Idle energy rate of ENERGY STAR electric fryer
|  |  | Large Vat |  |  | 1100
| [EFOODElec] |  |  |  |  | 167 | N | Wh/lb | ASTM energy to food
| [EffBaseElec] | Fryer Size | Standard Vat |  |  | 75% | N |  | Cooking efficiency of baseline electric fryer
|  |  | Large Vat |  |  | 70%
| [EffESTARElec] | Fryer Size | Standard Vat |  |  | 83% | Y |  | Cooking efficiency of ENERGY STAR electric fryer
|  |  | Large Vat |  |  | 80%
| [ΔkWh] | [5 empty] | C | kWh | Electric energy savings, calculated above
| [CF] |  |  |  |  | 0.787 | N |  | Summer peak coincidence factor
| [100,000] |  |  |  |  | 100000 | N | Btu to therms | Btu to therms conversion factor
| [ProductionBaseGas] | Fryer Size | Standard Vat |  |  | 60 | N | lb/hr | Production capacity of baseline gas fryer
|  |  | Large Vat |  |  | 100
| [ProductionESTARGas] | Fryer Size | Standard Vat |  |  | 65 | Y | lb/hr | Production capacity of ENERGY STAR gas fryer
|  |  | Large Vat |  |  | 110
| [IdleRateBaseGas] | Fryer Size | Standard Vat |  |  | 14000 | N | Btu/hr | Idle energy rate of baseline gas fryer
|  |  | Large Vat |  |  | 16000
| [IdleRateESTARGas] | Fryer Size | Standard Vat |  |  | 9000 | Y | Btu/hr | Idle energy rate of ENERGY STAR egas fryer
|  |  | Large Vat |  |  | 12000
| [EFOODGas] |  |  |  |  | 570 | N | Btu/lb | ASTM energy to food
| [EffBaseGas] |  |  |  |  | 35% | N |  | Cooking efficiency of baseline gas fryer
| [EffESTARGas] |  |  |  |  | 50% | Y |  | Cooking efficiency of ENERGY STAR gas fryer
| [Δtherms] | [5 empty] | C | therms | Natural gas energy savings, calculated above

## Griddle
Griddle
| Measure Code: | NR-FSE-ESGR-V01-170101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
12
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Griddle Type | Electric | 0
|  | Gas | 360
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([∆IdleEnergy] + [∆CookingEnergy]) * [Days] / [1,000]
| Time of Sale Demand (ΔkW) | =[∆kWh] / ([Hours] * [Days]) * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔIdleEnergy] | Cooker Fuel | Electric | = ([IdleRateBaseElec] * [Width] * [Length]* ([Hours] - [FoodCooked] / [ProductionBaseElec])) - ([IdleRateESTARElec] * [Width] * [Length] * ([Hours] - [FoodCooked] / [ProductionESTARElec]))
|  |  | Gas | = ([IdleRateBaseGas] * [Width] * [Length] * ([Hours] - [FoodCooked] / [ProductionBaseGas])) - ([IdleRateESTARGas] * [Width] * [Length] * ([Hours] - [FoodCooked] / [ProductionESTARGas]))
| [ΔCookingEnergy] | Cooker Fuel | Electric | = ([FoodCooked] * [EFOODElec] / [EffBaseElec]) - ([FoodCooked] * [EFOODElec] / [EffESTARElec])
|  |  | Gas | = ([FoodCooked] * [EFOODGas] / [EffBaseGas]) - ([FoodCooked] * [EFOODGas] / [EffESTARGas])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [∆kWh] |  |  |  |  | 1910.4 | C | kWh | Deemed value for electric griddle
| [Hours] |  |  |  |  | 12 | Y | Hours | Average daily hours of operation
| [Days] |  |  |  |  | 365.25 | Y | Days | Annual days of operation
| [1,000] |  |  |  |  | 1000 | N | Wh to kWh | Wh to kWh conversion factor
| [Width] |  |  |  |  | 3 | Y | ft | Griddle width
| [Depth] |  |  |  |  | 2 | Y | ft | Griddle depth
| [FoodCooked] |  |  |  |  | 100 | Y | lbs | Food cooked per day
| [ProductionBaseElec] |  |  |  |  | 35 | N | lb/hr | Production capacity of baseline electric griddle
| [ProductionESTARElec] |  |  |  |  | 40 | Y | lb/hr | Production capacity of ENERGY STAR electric griddle
| [IdleRateBaseElec] |  |  |  |  | 400 | N | W/ft2 | Idle energy rate of baseline electric griddle
| [IdleRateESTARElec] |  |  |  |  | 320 | Y | W/ft2 | Idle energy rate of ENERGY STAR electric griddle
| [EFOODElec] |  |  |  |  | 139 | N | Wh/lb | ASTM energy to food
| [EffBaseElec] |  |  |  |  | 65% | N |  | Cooking efficiency of baseline electric griddle
| [EffESTARElec] |  |  |  |  | 70% | Y |  | Cooking efficiency of ENERGY STAR electric griddle
| [ΔkWh] | [5 empty] | C | kWh | Electric energy savings, calculated above
| [CF] |  |  |  |  | 0.787 | N |  | Summer peak coincidence factor
| [Δtherms] |  |  |  |  | 131.4 | C | therms | Deemed value for gas griddle
| [100,000] |  |  |  |  | 100000 | N | Btu to therms | Btu to therms conversion factor
| [ProductionBaseGas] |  |  |  |  | 25 | N | lb/hr | Production capacity of baseline gas griddle
| [ProductionESTARGas] |  |  |  |  | 45 | Y | lb/hr | Production capacity of ENERGY STAR gas griddle
| [IdleRateBaseGas] |  |  |  |  | 3500 | N | Btu/hr/ft2 | Idle energy rate of baseline gas griddle
| [IdleRateESTARGas] |  |  |  |  | 2650 | Y | Btu/hr/ft2 | Idle energy rate of ENERGY STAR gas griddle
| [EFOODGas] |  |  |  |  | 475 | N | Btu/lb | ASTM energy to food
| [EffBaseGas] |  |  |  |  | 32% | N |  | Cooking efficiency of baseline gas griddle
| [EffESTARGas] |  |  |  |  | 38% | N |  | Cooking efficiency of ENERGY STAR gas griddle
| [Δtherms] | [5 empty] | C | therms | Natural gas energy savings, calculated above

## Infiltration Control - Test
Infiltration Control - Test
| Measure Code: | NR-SHL-AIRS-V04-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [∆kWh_cooling] + [∆kWh_heating]
| Time of Sale Demand (ΔkW) | = ([∆kWhcooling]) / [LHcooling] * [CF]
| Time of Sale Gas (ΔTherms) | = (([CFM_Pre] - [CFM_Post]) * [60] * [LH_heating] * [∆T_AVG,heating] * [0.018]) / (([η_heating_gas] * [100,000]))
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [∆kWh_cooling] |  |  | = (([CFM_Pre] - [CFM_Post]) * [60] * [LH_cooling] * [∆T_AVG,cooling] * [0.018] * [LM]) / (([1000] * [η_cooling]))
| [∆kWh_heating] | Heating Type | Electric | = (([CFM_Pre] - [CFM_Post]) * [60] * [LH_heating] * [∆T_AVG,heating] *[ 0.018]) / (([η_heating_elec] * [3,412]))
|  |  | Gas | = [∆Therms] * [Fe] * [29.3]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [CFMPre] | [5 empty] | Y |  | Infiltration at natural conditions as estimated by blower door testing before air sealing
| [CFMPost] | [5 empty] | Y |  | Infiltration at natural conditions as estimated by blower door testing after air sealing
| [60] | [5 empty] | 60 | ft3/min to ft3/hr | Converts Cubic Feet per Minute to Cubic Feet per Hour
| [LHCool] | Building Type | Convenience | Climate Zone | Zone 5 (Burlington) | 3005 | N | Hours | Load Hours for cooling
|  |  | Education |  |  | 3354
|  |  | Grocery |  |  | 2871
|  |  | Health |  |  | 5240
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 3537
|  |  | Lodging |  |  | 8019
|  |  | Multifamily |  |  | 5424
|  |  | Office - Large |  |  | 4844
|  |  | Office - Small |  |  | 3941
|  |  | Religious |  |  | 4347
|  |  | Restaurant |  |  | 3019
|  |  | Retail - Large |  |  | 3621
|  |  | Retail - Small |  |  | 2636
|  |  | Warehouse |  |  | 3617
|  |  | Nonresidential Average |  |  | 3643
|  |  | Convenience |  | Zone 6 (Mason City) | 4054
|  |  | Education |  |  | 2771
|  |  | Grocery |  |  | 2425
|  |  | Health |  |  | 4405
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 4526
|  |  | Lodging |  |  | 7309
|  |  | Multifamily |  |  | 4575
|  |  | Office - Large |  |  | 4457
|  |  | Office - Small |  |  | 3265
|  |  | Religious |  |  | 5267
|  |  | Restaurant |  |  | 2217
|  |  | Retail - Large |  |  | 4623
|  |  | Retail - Small |  |  | 1839
|  |  | Warehouse |  |  | 4553
|  |  | Nonresidential Average |  |  | 3732
|  |  | Convenience |  | Average/Unknown | 3628
|  |  | Education |  |  | 2996
|  |  | Grocery |  |  | 2725
|  |  | Health |  |  | 4770
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 3977
|  |  | Lodging |  |  | 7909
|  |  | Multifamily |  |  | 5084
|  |  | Office - Large |  |  | 4596
|  |  | Office - Small |  |  | 3678
|  |  | Religious |  |  | 4763
|  |  | Restaurant |  |  | 2798
|  |  | Retail - Large |  |  | 4218
|  |  | Retail - Small |  |  | 2445
|  |  | Warehouse |  |  | 4100
|  |  | Nonresidential Average |  |  | 3734
| [ΔTAVG,cooling] | Climate Zone | Zone 5 (Burlington) |  |  | 5.4 | N | ⁰F | Average temperature difference [⁰F] during cooling season between outdoor air temperature and assumed 75⁰F indoor air temperature
|  |  | Zone 6 (Mason City) |  |  | 0.2
|  |  | Average/Unknown |  |  | 3.6
| [0.018] |  |  |  |  | 0.018 | N | Btu/ft3*°F | Specific Heat Capacity of Air (Btu/ft3*°F)
| [LM] | Climate Zone | Zone 5 (Burlington) |  |  | 4.1 | N |  | Latent multiplier to account for latent cooling demand
|  |  | Zone 6 (Mason City) |  |  | 4.2
|  |  | Average/Unknown |  |  | 4.2
| [1,000] |  |  |  |  | 1000 | N | Btu to kBtu | Btu to kBtu conversion factor
| [ηcooling] | [5 empty] | Y | kBtu/kWh | Energy efficiency ratio (EER) of cooling system (kBtu/kWh)
| [LHHeat] | Building Type | Convenience | Climate Zone | Zone 5 (Burlington) | 3024 | N | Hours | Load Hours for heating space
|  |  | Education |  |  | 6213
|  |  | Grocery |  |  | 6217
|  |  | Health |  |  | 8729
|  |  | Hospital |  |  | 8286
|  |  | Industrial |  |  | 3396
|  |  | Lodging |  |  | 5218
|  |  | Multifamily |  |  | 5145
|  |  | Office - Large |  |  | 5037
|  |  | Office - Small |  |  | 4641
|  |  | Religious |  |  | 2485
|  |  | Restaurant |  |  | 2954
|  |  | Retail - Large |  |  | 2699
|  |  | Retail - Small |  |  | 4222
|  |  | Warehouse |  |  | 2025
|  |  | Nonresidential Average |  |  | 3480
|  |  | Convenience |  | Zone 6 (Mason City) | 2129
|  |  | Education |  |  | 6633
|  |  | Grocery |  |  | 6819
|  |  | Health |  |  | 8732
|  |  | Hospital |  |  | 8272
|  |  | Industrial |  |  | 2233
|  |  | Lodging |  |  | 6234
|  |  | Multifamily |  |  | 5998
|  |  | Office - Large |  |  | 5787
|  |  | Office - Small |  |  | 5329
|  |  | Religious |  |  | 1667
|  |  | Restaurant |  |  | 3619
|  |  | Retail - Large |  |  | 1807
|  |  | Retail - Small |  |  | 4935
|  |  | Warehouse |  |  | 1390
|  |  | Nonresidential Average |  |  | 3473
|  |  | Convenience |  | Average/Unknown | 2690
|  |  | Education |  |  | 6430
|  |  | Grocery |  |  | 6499
|  |  | Health |  |  | 8720
|  |  | Hospital |  |  | 8289
|  |  | Industrial |  |  | 3080
|  |  | Lodging |  |  | 5500
|  |  | Multifamily |  |  | 5382
|  |  | Office - Large |  |  | 5316
|  |  | Office - Small |  |  | 5087
|  |  | Religious |  |  | 2223
|  |  | Restaurant |  |  | 3321
|  |  | Retail - Large |  |  | 2405
|  |  | Retail - Small |  |  | 4596
|  |  | Warehouse |  |  | 1788
|  |  | Nonresidential Average |  |  | 3561
| [ΔTAVG,heating] | Climate Zone | Zone 5 (Burlington) |  |  | 15.4 | N | ⁰F | Average temperature difference [⁰F] during heating season between outdoor air temperature and assumed 55⁰F heating base temperature
|  |  | Zone 6 (Mason City) |  |  | 24.9
|  |  | Average/Unknown |  |  | 19.1
| [3,142] |  |  |  |  | 3142 | N | Btu to kWh | Conversion from Btu to kWh.
| [η_heating_elec] | [5 empty] | Y |  | Efficiency of heating system, expressed as COP
| [∆kWh_heating] | [5 empty] | C | kWh | If gas furnace heat, kWh savings for reduction in fan run time
| [Fe] |  |  |  |  | 3.14% | N |  | Furnace Fan energy consumption as a percentage of annual fuel consumption
| [29.3] |  |  |  |  | 29.3 | N | kWh per therm | kWh per therm
| [CF] | Building Type | Convenience |  |  | 92.3% | N |  | Summer System Peak Coincidence Factor for Cooling (dependent on building type)
|  |  | Education |  |  | 96.7%
|  |  | Grocery |  |  | 100%
|  |  | Health |  |  | 100%
|  |  | Hospital |  |  | 98.6%
|  |  | Industrial |  |  | 44.6%
|  |  | Lodging |  |  | 97.4%
|  |  | Multifamily |  |  | 100%
|  |  | Office - Large |  |  | 98.8%
|  |  | Office - Small |  |  | 100%
|  |  | Religious |  |  | 94.3%
|  |  | Restaurant |  |  | 99.6%
|  |  | Retail - Large |  |  | 87.6%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 77.9%
|  |  | Nonresidential Average |  |  | 92.3%
| [η_heating_gas] | [5 empty] | Y |  | Efficiency of gas heating system
| [100,000] |  |  |  |  | 100000 | N | Btu to therms | Btu to therms conversion factor
| [Δtherms] | [5 empty] | C | therms | Natural gas energy savings, calculated above
| [GCF] | Building Type | Convenience |  |  | 0.016482 | N |  | Gas Coincidence Factor for Heating
|  |  | Education |  |  | 0.01148
|  |  | Grocery |  |  | 0.013083
|  |  | Health |  |  | 0.010179
|  |  | Hospital |  |  | 0.015543
|  |  | Industrial |  |  | 0.014296
|  |  | Lodging |  |  | 0.013205
|  |  | Multifamily |  |  | 0.012268
|  |  | Office - Large |  |  | 0.013082
|  |  | Office - Small |  |  | 0.016718
|  |  | Religious |  |  | 0.011964
|  |  | Restaurant |  |  | 0.015262
|  |  | Retail - Large |  |  | 0.013281
|  |  | Retail - Small |  |  | 0.014055
|  |  | Warehouse |  |  | 0.015677
|  |  | Nonresidential Average |  |  | 0.014658

## Infiltration Control - Deemed
Infiltration Control - Deemed
| Measure Code: | NR-SHL-AIRS-V04-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [SavingsPerUnit] * [SqFt]
| Time of Sale Demand (ΔkW) | = ([∆kWhcooling]) / [LHcooling] * [CF]
| Time of Sale Gas (ΔTherms) | = [SavingsPerUnit] * [SqFt]
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [SavingsPerUnit] | End Use | Cooling Chillers | HVAC System | Chiller | 0.027 | N | kWh/ft2 | Annual savings per square foot, dependent on heating / cooling equipment
|  |  | Cooling DX |  | Air Conditioning | 0.041
|  |  | Space Heat |  | Electric Resistance /Furnace | 0.2915
|  |  | Heat Pump - Cooling |  | Heat Pump | 0.041
|  |  | Heat Pump - Heating |  |  | 0.1885
|  |  | Space Heat Boiler |  | Gas Boiler | 0.01555
|  |  | Space Heat Furnace |  | Gas Furnace | 0.01555
| [SqFt] | [5 empty] | Y | ft2 | Building square footage
| [∆kWhcooling] | [5 empty] | C | kWh | Calculation of savings of cooling system as above
| [LHCool] | Building Type | Convenience | Climate Zone | Zone 5 (Burlington) | 3005 | N | Hours | Load Hours for cooling
|  |  | Education |  |  | 3354
|  |  | Grocery |  |  | 2871
|  |  | Health |  |  | 5240
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 3537
|  |  | Lodging |  |  | 8019
|  |  | Multifamily |  |  | 5424
|  |  | Office - Large |  |  | 4844
|  |  | Office - Small |  |  | 3941
|  |  | Religious |  |  | 4347
|  |  | Restaurant |  |  | 3019
|  |  | Retail - Large |  |  | 3621
|  |  | Retail - Small |  |  | 2636
|  |  | Warehouse |  |  | 3617
|  |  | Nonresidential Average |  |  | 3643
|  |  | Convenience |  | Zone 6 (Mason City) | 4054
|  |  | Education |  |  | 2771
|  |  | Grocery |  |  | 2425
|  |  | Health |  |  | 4405
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 4526
|  |  | Lodging |  |  | 7309
|  |  | Multifamily |  |  | 4575
|  |  | Office - Large |  |  | 4457
|  |  | Office - Small |  |  | 3265
|  |  | Religious |  |  | 5267
|  |  | Restaurant |  |  | 2217
|  |  | Retail - Large |  |  | 4623
|  |  | Retail - Small |  |  | 1839
|  |  | Warehouse |  |  | 4553
|  |  | Nonresidential Average |  |  | 3732
|  |  | Convenience |  | Average/Unknown | 3628
|  |  | Education |  |  | 2996
|  |  | Grocery |  |  | 2725
|  |  | Health |  |  | 4770
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 3977
|  |  | Lodging |  |  | 7909
|  |  | Multifamily |  |  | 5084
|  |  | Office - Large |  |  | 4596
|  |  | Office - Small |  |  | 3678
|  |  | Religious |  |  | 4763
|  |  | Restaurant |  |  | 2798
|  |  | Retail - Large |  |  | 4218
|  |  | Retail - Small |  |  | 2445
|  |  | Warehouse |  |  | 4100
|  |  | Nonresidential Average |  |  | 3734
| [CF] | Building Type | Convenience |  |  | 92.3% | N |  | Summer System Peak Coincidence Factor for Cooling (dependent on building type)
|  |  | Education |  |  | 96.7%
|  |  | Grocery |  |  | 100%
|  |  | Health |  |  | 100%
|  |  | Hospital |  |  | 98.6%
|  |  | Industrial |  |  | 44.6%
|  |  | Lodging |  |  | 97.4%
|  |  | Multifamily |  |  | 100%
|  |  | Office - Large |  |  | 98.8%
|  |  | Office - Small |  |  | 100%
|  |  | Religious |  |  | 94.3%
|  |  | Restaurant |  |  | 99.6%
|  |  | Retail - Large |  |  | 87.6%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 77.9%
|  |  | Nonresidential Average |  |  | 92.3%
| [Δtherms] | [5 empty] | C | therms | Natural gas energy savings, calculated above
| [GCF] | Building Type | Convenience |  |  | 0.016482 | N |  | Gas Coincidence Factor for Heating
|  |  | Education |  |  | 0.01148
|  |  | Grocery |  |  | 0.013083
|  |  | Health |  |  | 0.010179
|  |  | Hospital |  |  | 0.015543
|  |  | Industrial |  |  | 0.014296
|  |  | Lodging |  |  | 0.013205
|  |  | Multifamily |  |  | 0.012268
|  |  | Office - Large |  |  | 0.013082
|  |  | Office - Small |  |  | 0.016718
|  |  | Religious |  |  | 0.011964
|  |  | Restaurant |  |  | 0.015262
|  |  | Retail - Large |  |  | 0.013281
|  |  | Retail - Small |  |  | 0.014055
|  |  | Warehouse |  |  | 0.015677
|  |  | Nonresidential Average |  |  | 0.014658

## Foundation Wall Insulation
Foundation Wall Insulation
| Measure Code: | NR-SHL-FINS-V04-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
20
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [∆kWhcooling] + [∆kWhheating]
| Time of Sale Demand (ΔkW) | = ([∆kWhcooling] / [LHcooling]) * [CF]
| Time of Sale Gas (ΔTherms) | = ((((1 / [R_existingAG] - 1 / [R_newAG]) * [Area_AG]) + (( 1 / [R_existingBG] - 1 / [R_newBG ]) * [Area_BG])) * [LH_heating] * [∆T_AVG,heating])) / (([100,000] * [η_heat_gas]))
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [∆kWh_cooling] |  |  | = ((1 / [R_existingAG] - 1 / [R_newAG]) *[ Area_AG] * [LH_cooling] * [∆T_AVG,cooling]) / (([1,000] * [η_cooling]))
| [∆kWh_heating] | Fuel Type | Electric (resistance or heat pump) | = ((((1 / [R_existingAG] - 1 / [R_newAG]) * [Area_AG ]) + ((1 / [R_existingBG] - 1 / [R_newBG]) *[ Area_BG])) * [LH_heating] * [∆T_AVG,heating])) / (([3,412] * [η_heating_elec]))
|  |  | Gas | = [∆Therms] * [Fe] * [29.3]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [RexistingAG] | [5 empty] | Y | hr-⁰F-ft2)/Btu | Above grade wall heat loss coefficient with existing insulation for complete structural assembly [(hr-⁰F-ft2)/Btu]
| [RnewAG] | [5 empty] | Y | hr-⁰F-ft2)/Btu | Above grade wall heat loss coefficient with new insulation for complete structural assembly [(hr-⁰F-ft2)/Btu]
| [AreaAG] | [5 empty] | Y | ft2 | Area of the above grade wall surface in square feet.
| [LHCool] | Building Type | Convenience | Climate Zone | Zone 5 (Burlington) | 3005 | N | Hours | Load Hours for cooling
|  |  | Education |  |  | 3354
|  |  | Grocery |  |  | 2871
|  |  | Health |  |  | 5240
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 3537
|  |  | Lodging |  |  | 8019
|  |  | Multifamily |  |  | 5424
|  |  | Office - Large |  |  | 4844
|  |  | Office - Small |  |  | 3941
|  |  | Religious |  |  | 4347
|  |  | Restaurant |  |  | 3019
|  |  | Retail - Large |  |  | 3621
|  |  | Retail - Small |  |  | 2636
|  |  | Warehouse |  |  | 3617
|  |  | Nonresidential Average |  |  | 3643
|  |  | Convenience |  | Zone 6 (Mason City) | 4054
|  |  | Education |  |  | 2771
|  |  | Grocery |  |  | 2425
|  |  | Health |  |  | 4405
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 4526
|  |  | Lodging |  |  | 7309
|  |  | Multifamily |  |  | 4575
|  |  | Office - Large |  |  | 4457
|  |  | Office - Small |  |  | 3265
|  |  | Religious |  |  | 5267
|  |  | Restaurant |  |  | 2217
|  |  | Retail - Large |  |  | 4623
|  |  | Retail - Small |  |  | 1839
|  |  | Warehouse |  |  | 4553
|  |  | Nonresidential Average |  |  | 3732
|  |  | Convenience |  | Average/Unknown | 3628
|  |  | Education |  |  | 2996
|  |  | Grocery |  |  | 2725
|  |  | Health |  |  | 4770
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 3977
|  |  | Lodging |  |  | 7909
|  |  | Multifamily |  |  | 5084
|  |  | Office - Large |  |  | 4596
|  |  | Office - Small |  |  | 3678
|  |  | Religious |  |  | 4763
|  |  | Restaurant |  |  | 2798
|  |  | Retail - Large |  |  | 4218
|  |  | Retail - Small |  |  | 2445
|  |  | Warehouse |  |  | 4100
|  |  | Nonresidential Average |  |  | 3734
| [ΔTAVG,cooling] | Climate Zone | Zone 5 (Burlington) |  |  | 5.4 | N | ⁰F | Average temperature difference [⁰F] during cooling season between outdoor air temperature and assumed 75⁰F indoor air temperature
|  |  | Zone 6 (Mason City) |  |  | 0.2
|  |  | Average/Unknown |  |  | 3.6
| [1,000] |  |  |  |  | 1000 | N | Btu to kBtu | Btu to kBtu conversion factor
| [ηcooling] | [5 empty] | Y | kBtu/kWh | Seasonal energy efficiency ratio (SEER) of cooling system (kBtu/kWh)
| [RexistingBG] | [5 empty] | Y | hr-⁰F-ft2)/Btu | Below grade wall assembly heat loss coefficient with existing insulation [(hr-⁰F-ft2)/Btu]
| [RnewBG] | [5 empty] | Y | hr-⁰F-ft2)/Btu | Below grade wall assembly heat loss coefficient with new insulation [(hr-⁰F-ft2)/Btu]
| [AreaBG] | [5 empty] | Y | ft2 | Area of the below grade wall surface in square feet.
| [LHHeat] | Building Type | Convenience | Climate Zone | Zone 5 (Burlington) | 3024 | N | Hours | Load Hours for heating space
|  |  | Education |  |  | 6213
|  |  | Grocery |  |  | 6217
|  |  | Health |  |  | 8729
|  |  | Hospital |  |  | 8286
|  |  | Industrial |  |  | 3396
|  |  | Lodging |  |  | 5218
|  |  | Multifamily |  |  | 5145
|  |  | Office - Large |  |  | 5037
|  |  | Office - Small |  |  | 4641
|  |  | Religious |  |  | 2485
|  |  | Restaurant |  |  | 2954
|  |  | Retail - Large |  |  | 2699
|  |  | Retail - Small |  |  | 4222
|  |  | Warehouse |  |  | 2025
|  |  | Nonresidential Average |  |  | 3480
|  |  | Convenience |  | Zone 6 (Mason City) | 2129
|  |  | Education |  |  | 6633
|  |  | Grocery |  |  | 6819
|  |  | Health |  |  | 8732
|  |  | Hospital |  |  | 8272
|  |  | Industrial |  |  | 2233
|  |  | Lodging |  |  | 6234
|  |  | Multifamily |  |  | 5998
|  |  | Office - Large |  |  | 5787
|  |  | Office - Small |  |  | 5329
|  |  | Religious |  |  | 1667
|  |  | Restaurant |  |  | 3619
|  |  | Retail - Large |  |  | 1807
|  |  | Retail - Small |  |  | 4935
|  |  | Warehouse |  |  | 1390
|  |  | Nonresidential Average |  |  | 3473
|  |  | Convenience |  | Average/Unknown | 2690
|  |  | Education |  |  | 6430
|  |  | Grocery |  |  | 6499
|  |  | Health |  |  | 8720
|  |  | Hospital |  |  | 8289
|  |  | Industrial |  |  | 3080
|  |  | Lodging |  |  | 5500
|  |  | Multifamily |  |  | 5382
|  |  | Office - Large |  |  | 5316
|  |  | Office - Small |  |  | 5087
|  |  | Religious |  |  | 2223
|  |  | Restaurant |  |  | 3321
|  |  | Retail - Large |  |  | 2405
|  |  | Retail - Small |  |  | 4596
|  |  | Warehouse |  |  | 1788
|  |  | Nonresidential Average |  |  | 3561
| [ΔTAVG,heating] | Climate Zone | Zone 5 (Burlington) |  |  | 15.4 | N | ⁰F | Average temperature difference [⁰F] during heating season between outdoor air temperature and assumed 55⁰F heating base temperature
|  |  | Zone 6 (Mason City) |  |  | 24.9
|  |  | Average/Unknown |  |  | 19.1
| [3,142] |  |  |  |  | 3142 | N | Btu to kWh | Conversion from Btu to kWh.
| [η_heating_elec] | [5 empty] | Y |  | Efficiency of electric heating system
| [∆Therms] | [5 empty] | C | Therms | Gas savings calcualted with equation below
| [Fe] |  |  |  |  | 3.14% | N |  | Furnace Fan energy consumption as a percentage of annual fuel consumption
| [29.3] |  |  |  |  | 29.3 | N | kWh per therm | kWh per therm
| [CF] | Building Type | Convenience |  |  | 92.3% | N |  | Summer System Peak Coincidence Factor for Cooling (dependent on building type)
|  |  | Education |  |  | 96.7%
|  |  | Grocery |  |  | 100%
|  |  | Health |  |  | 100%
|  |  | Hospital |  |  | 98.6%
|  |  | Industrial |  |  | 44.6%
|  |  | Lodging |  |  | 97.4%
|  |  | Multifamily |  |  | 100%
|  |  | Office - Large |  |  | 98.8%
|  |  | Office - Small |  |  | 100%
|  |  | Religious |  |  | 94.3%
|  |  | Restaurant |  |  | 99.6%
|  |  | Retail - Large |  |  | 87.6%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 77.9%
|  |  | Nonresidential Average |  |  | 92.3%
| [100,000] |  |  |  |  | 100000 | N | Btu to therms | Btu to therms conversion factor
| [η_heat_gas] | [5 empty] | Y |  | Efficiency of gas heating system
| [Δtherms] | [5 empty] | C | therms | Natural gas energy savings, calculated above
| [GCF] | Building Type | Convenience |  |  | 0.016482 | N |  | Gas Coincidence Factor for Heating
|  |  | Education |  |  | 0.01148
|  |  | Grocery |  |  | 0.013083
|  |  | Health |  |  | 0.010179
|  |  | Hospital |  |  | 0.015543
|  |  | Industrial |  |  | 0.014296
|  |  | Lodging |  |  | 0.013205
|  |  | Multifamily |  |  | 0.012268
|  |  | Office - Large |  |  | 0.013082
|  |  | Office - Small |  |  | 0.016718
|  |  | Religious |  |  | 0.011964
|  |  | Restaurant |  |  | 0.015262
|  |  | Retail - Large |  |  | 0.013281
|  |  | Retail - Small |  |  | 0.014055
|  |  | Warehouse |  |  | 0.015677
|  |  | Nonresidential Average |  |  | 0.014658

## Roof Insulation
Roof Insulation
| Measure Code: | NR-SHL-XINS-V05-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
20
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [∆kWhcooling] + [∆kWhheating]
| Time of Sale Demand (ΔkW) | = ([∆kWhcooling] / [LHcooling]) * [CF]
| Time of Sale Gas (ΔTherms) | = ((1 / [R_existing] - 1 / [R_new]) * [Area] * [LH_heating] * [∆T_AVG,heating]) / ([100,000] * [η_heat_gas])
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [∆kWh_cooling] |  |  | = ((1 / [R_existing] - 1 / [R_new]) *[ Area] * [LH_cooling] * [∆T_AVG,cooling]) / (([1,000] * [η_cooling]))
| [∆kWh_heating] | Fuel Type | Electric (resistance or heat pump) | = ((1 / [R_existing] - 1 / [R_new]) * [Area]) * [LH_heating] * [∆T_AVG,heating]) / ([3,412] * [η_heating_elec])
|  |  | Gas | = [∆Therms] * [Fe] * [29.3]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Rexisting] | [5 empty] | Y | (['hr-⁰F-ft2)/Btu | Complete Roof assembly heat loss coefficient with existing insulation (or code baseline for NC) [(hr-⁰F-ft2)/Btu]
| [Rnew] | [5 empty] | Y | (['hr-⁰F-ft2)/Btu | Complete Roof assembly heat loss coefficient with new insulation [(hr-⁰F-ft2)/Btu]
| [Area] | [5 empty] | Y | ft2 | Area of the insulated roof surface in square feet, as measured from within the conditioned space (area of overhangs or eaves should be excluded, for example).
| [LHCool] | Building Type | Convenience | Climate Zone | Zone 5 (Burlington) | 3005 | N | Hours | Load Hours for cooling
|  |  | Education |  |  | 3354
|  |  | Grocery |  |  | 2871
|  |  | Health |  |  | 5240
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 3537
|  |  | Lodging |  |  | 8019
|  |  | Multifamily |  |  | 5424
|  |  | Office - Large |  |  | 4844
|  |  | Office - Small |  |  | 3941
|  |  | Religious |  |  | 4347
|  |  | Restaurant |  |  | 3019
|  |  | Retail - Large |  |  | 3621
|  |  | Retail - Small |  |  | 2636
|  |  | Warehouse |  |  | 3617
|  |  | Nonresidential Average |  |  | 3643
|  |  | Convenience |  | Zone 6 (Mason City) | 4054
|  |  | Education |  |  | 2771
|  |  | Grocery |  |  | 2425
|  |  | Health |  |  | 4405
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 4526
|  |  | Lodging |  |  | 7309
|  |  | Multifamily |  |  | 4575
|  |  | Office - Large |  |  | 4457
|  |  | Office - Small |  |  | 3265
|  |  | Religious |  |  | 5267
|  |  | Restaurant |  |  | 2217
|  |  | Retail - Large |  |  | 4623
|  |  | Retail - Small |  |  | 1839
|  |  | Warehouse |  |  | 4553
|  |  | Nonresidential Average |  |  | 3732
|  |  | Convenience |  | Average/Unknown | 3628
|  |  | Education |  |  | 2996
|  |  | Grocery |  |  | 2725
|  |  | Health |  |  | 4770
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 3977
|  |  | Lodging |  |  | 7909
|  |  | Multifamily |  |  | 5084
|  |  | Office - Large |  |  | 4596
|  |  | Office - Small |  |  | 3678
|  |  | Religious |  |  | 4763
|  |  | Restaurant |  |  | 2798
|  |  | Retail - Large |  |  | 4218
|  |  | Retail - Small |  |  | 2445
|  |  | Warehouse |  |  | 4100
|  |  | Nonresidential Average |  |  | 3734
| [ΔTAVG,cooling] | Climate Zone | Zone 5 (Burlington) |  |  | 5.4 | N | ⁰F | Average temperature difference [⁰F] during cooling season between outdoor air temperature and assumed 75⁰F indoor air temperature
|  |  | Zone 6 (Mason City) |  |  | 0.2
|  |  | Average/Unknown |  |  | 3.6
| [1,000] |  |  |  |  | 1000 | N | Btu to kBtu | Btu to kBtu conversion factor
| [ηcooling] | [5 empty] | Y | kBtu/kWh | Seasonal energy efficiency ratio (SEER) of cooling system (kBtu/kWh)
| [LHHeat] | Building Type | Convenience | Climate Zone | Zone 5 (Burlington) | 3024 | N | Hours | Load Hours for heating space
|  |  | Education |  |  | 6213
|  |  | Grocery |  |  | 6217
|  |  | Health |  |  | 8729
|  |  | Hospital |  |  | 8286
|  |  | Industrial |  |  | 3396
|  |  | Lodging |  |  | 5218
|  |  | Multifamily |  |  | 5145
|  |  | Office - Large |  |  | 5037
|  |  | Office - Small |  |  | 4641
|  |  | Religious |  |  | 2485
|  |  | Restaurant |  |  | 2954
|  |  | Retail - Large |  |  | 2699
|  |  | Retail - Small |  |  | 4222
|  |  | Warehouse |  |  | 2025
|  |  | Nonresidential Average |  |  | 3480
|  |  | Convenience |  | Zone 6 (Mason City) | 2129
|  |  | Education |  |  | 6633
|  |  | Grocery |  |  | 6819
|  |  | Health |  |  | 8732
|  |  | Hospital |  |  | 8272
|  |  | Industrial |  |  | 2233
|  |  | Lodging |  |  | 6234
|  |  | Multifamily |  |  | 5998
|  |  | Office - Large |  |  | 5787
|  |  | Office - Small |  |  | 5329
|  |  | Religious |  |  | 1667
|  |  | Restaurant |  |  | 3619
|  |  | Retail - Large |  |  | 1807
|  |  | Retail - Small |  |  | 4935
|  |  | Warehouse |  |  | 1390
|  |  | Nonresidential Average |  |  | 3473
|  |  | Convenience |  | Average/Unknown | 2690
|  |  | Education |  |  | 6430
|  |  | Grocery |  |  | 6499
|  |  | Health |  |  | 8720
|  |  | Hospital |  |  | 8289
|  |  | Industrial |  |  | 3080
|  |  | Lodging |  |  | 5500
|  |  | Multifamily |  |  | 5382
|  |  | Office - Large |  |  | 5316
|  |  | Office - Small |  |  | 5087
|  |  | Religious |  |  | 2223
|  |  | Restaurant |  |  | 3321
|  |  | Retail - Large |  |  | 2405
|  |  | Retail - Small |  |  | 4596
|  |  | Warehouse |  |  | 1788
|  |  | Nonresidential Average |  |  | 3561
| [ΔTAVG,heating] | Climate Zone | Zone 5 (Burlington) |  |  | 15.4 | N | ⁰F | Average temperature difference [⁰F] during heating season between outdoor air temperature and assumed 55⁰F heating base temperature
|  |  | Zone 6 (Mason City) |  |  | 24.9
|  |  | Average/Unknown |  |  | 19.1
| [3,142] |  |  |  |  | 3142 | N | Btu to kWh | Conversion from Btu to kWh.
| [η_heating_elec] | [5 empty] | Y |  | Efficiency of electric heating system
| [∆Therms] | [5 empty] | C | Therms | Gas savings calcualted with equation below
| [Fe] |  |  |  |  | 3.14% | N |  | Furnace Fan energy consumption as a percentage of annual fuel consumption
| [29.3] |  |  |  |  | 29.3 | N | kWh per therm | kWh per therm
| [CF] | Building Type | Convenience |  |  | 92.3% | N |  | Summer System Peak Coincidence Factor for Cooling (dependent on building type)
|  |  | Education |  |  | 96.7%
|  |  | Grocery |  |  | 100%
|  |  | Health |  |  | 100%
|  |  | Hospital |  |  | 98.6%
|  |  | Industrial |  |  | 44.6%
|  |  | Lodging |  |  | 97.4%
|  |  | Multifamily |  |  | 100%
|  |  | Office - Large |  |  | 98.8%
|  |  | Office - Small |  |  | 100%
|  |  | Religious |  |  | 94.3%
|  |  | Restaurant |  |  | 99.6%
|  |  | Retail - Large |  |  | 87.6%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 77.9%
|  |  | Nonresidential Average |  |  | 92.3%
| [100,000] |  |  |  |  | 100000 | N | Btu to therms | Btu to therms conversion factor
| [η_heating_gas] | [5 empty] | Y |  | Efficiency of has heating system
| [Δtherms] | [5 empty] | C | therms | Natural gas energy savings, calculated above
| [GCF] | Building Type | Convenience |  |  | 0.016482 | N |  | Gas Coincidence Factor for Heating
|  |  | Education |  |  | 0.01148
|  |  | Grocery |  |  | 0.013083
|  |  | Health |  |  | 0.010179
|  |  | Hospital |  |  | 0.015543
|  |  | Industrial |  |  | 0.014296
|  |  | Lodging |  |  | 0.013205
|  |  | Multifamily |  |  | 0.012268
|  |  | Office - Large |  |  | 0.013082
|  |  | Office - Small |  |  | 0.016718
|  |  | Religious |  |  | 0.011964
|  |  | Restaurant |  |  | 0.015262
|  |  | Retail - Large |  |  | 0.013281
|  |  | Retail - Small |  |  | 0.014055
|  |  | Warehouse |  |  | 0.015677
|  |  | Nonresidential Average |  |  | 0.014658

## Wall Insulation
Wall Insulation
| Measure Code: | NR-SHL-WINS-V03-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
20
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [∆kWhcooling] + [∆kWhheating]
| Time of Sale Demand (ΔkW) | = ([∆kWhcooling] / [LHcooling]) * [CF]
| Time of Sale Gas (ΔTherms) | = ((1 / [R_existing] - 1 / [R_new]) * [Area] * [LH_heating] * [∆T_AVG,heating]) / ([100,000] * [η_heat_gas])
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [∆kWh_cooling] |  |  | = ((1 / [R_existing] - 1 / [R_new]) *[ Area] * [LH_cooling] * [∆T_AVG,cooling]) / (([1,000] * [η_cooling]))
| [∆kWh_heating] | Fuel Type | Electric (resistance or heat pump) | = ((1 / [R_existing] - 1 / [R_new]) * [Area]) * [LH_heating] * [∆T_AVG,heating]) / ([3,412] * [η_heating_elec])
|  |  | Gas | = [∆Therms] * [Fe] * [29.3]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Rexisting] | [5 empty] | Y | (['hr-⁰F-ft2)/Btu | Complete Wall assembly heat loss coefficient with existing insulation [(hr-⁰F-ft2)/Btu]
| [Rnew] | [5 empty] | Y | (['hr-⁰F-ft2)/Btu | Complete Wall assembly heat loss coefficient with new insulation [(hr-⁰F-ft2)/Btu]
| [Area] | [5 empty] | Y | ft2 | Area of the wall surface in square feet.
| [LHCool] | Building Type | Convenience | Climate Zone | Zone 5 (Burlington) | 3005 | N | Hours | Load Hours for cooling
|  |  | Education |  |  | 3354
|  |  | Grocery |  |  | 2871
|  |  | Health |  |  | 5240
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 3537
|  |  | Lodging |  |  | 8019
|  |  | Multifamily |  |  | 5424
|  |  | Office - Large |  |  | 4844
|  |  | Office - Small |  |  | 3941
|  |  | Religious |  |  | 4347
|  |  | Restaurant |  |  | 3019
|  |  | Retail - Large |  |  | 3621
|  |  | Retail - Small |  |  | 2636
|  |  | Warehouse |  |  | 3617
|  |  | Nonresidential Average |  |  | 3643
|  |  | Convenience |  | Zone 6 (Mason City) | 4054
|  |  | Education |  |  | 2771
|  |  | Grocery |  |  | 2425
|  |  | Health |  |  | 4405
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 4526
|  |  | Lodging |  |  | 7309
|  |  | Multifamily |  |  | 4575
|  |  | Office - Large |  |  | 4457
|  |  | Office - Small |  |  | 3265
|  |  | Religious |  |  | 5267
|  |  | Restaurant |  |  | 2217
|  |  | Retail - Large |  |  | 4623
|  |  | Retail - Small |  |  | 1839
|  |  | Warehouse |  |  | 4553
|  |  | Nonresidential Average |  |  | 3732
|  |  | Convenience |  | Average/Unknown | 3628
|  |  | Education |  |  | 2996
|  |  | Grocery |  |  | 2725
|  |  | Health |  |  | 4770
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 3977
|  |  | Lodging |  |  | 7909
|  |  | Multifamily |  |  | 5084
|  |  | Office - Large |  |  | 4596
|  |  | Office - Small |  |  | 3678
|  |  | Religious |  |  | 4763
|  |  | Restaurant |  |  | 2798
|  |  | Retail - Large |  |  | 4218
|  |  | Retail - Small |  |  | 2445
|  |  | Warehouse |  |  | 4100
|  |  | Nonresidential Average |  |  | 3734
| [ΔTAVG,cooling] | Climate Zone | Zone 5 (Burlington) |  |  | 5.4 | N | ⁰F | Average temperature difference [⁰F] during cooling season between outdoor air temperature and assumed 75⁰F indoor air temperature
|  |  | Zone 6 (Mason City) |  |  | 0.2
|  |  | Average/Unknown |  |  | 3.6
| [1,000] |  |  |  |  | 1000 | N | Btu to kBtu | Btu to kBtu conversion factor
| [ηcooling] | [5 empty] | Y | kBtu/kWh | Seasonal energy efficiency ratio (SEER) of cooling system (kBtu/kWh)
| [LHHeat] | Building Type | Convenience | Climate Zone | Zone 5 (Burlington) | 3024 | N | Hours | Load Hours for heating space
|  |  | Education |  |  | 6213
|  |  | Grocery |  |  | 6217
|  |  | Health |  |  | 8729
|  |  | Hospital |  |  | 8286
|  |  | Industrial |  |  | 3396
|  |  | Lodging |  |  | 5218
|  |  | Multifamily |  |  | 5145
|  |  | Office - Large |  |  | 5037
|  |  | Office - Small |  |  | 4641
|  |  | Religious |  |  | 2485
|  |  | Restaurant |  |  | 2954
|  |  | Retail - Large |  |  | 2699
|  |  | Retail - Small |  |  | 4222
|  |  | Warehouse |  |  | 2025
|  |  | Nonresidential Average |  |  | 3480
|  |  | Convenience |  | Zone 6 (Mason City) | 2129
|  |  | Education |  |  | 6633
|  |  | Grocery |  |  | 6819
|  |  | Health |  |  | 8732
|  |  | Hospital |  |  | 8272
|  |  | Industrial |  |  | 2233
|  |  | Lodging |  |  | 6234
|  |  | Multifamily |  |  | 5998
|  |  | Office - Large |  |  | 5787
|  |  | Office - Small |  |  | 5329
|  |  | Religious |  |  | 1667
|  |  | Restaurant |  |  | 3619
|  |  | Retail - Large |  |  | 1807
|  |  | Retail - Small |  |  | 4935
|  |  | Warehouse |  |  | 1390
|  |  | Nonresidential Average |  |  | 3473
|  |  | Convenience |  | Average/Unknown | 2690
|  |  | Education |  |  | 6430
|  |  | Grocery |  |  | 6499
|  |  | Health |  |  | 8720
|  |  | Hospital |  |  | 8289
|  |  | Industrial |  |  | 3080
|  |  | Lodging |  |  | 5500
|  |  | Multifamily |  |  | 5382
|  |  | Office - Large |  |  | 5316
|  |  | Office - Small |  |  | 5087
|  |  | Religious |  |  | 2223
|  |  | Restaurant |  |  | 3321
|  |  | Retail - Large |  |  | 2405
|  |  | Retail - Small |  |  | 4596
|  |  | Warehouse |  |  | 1788
|  |  | Nonresidential Average |  |  | 3561
| [ΔTAVG,heating] | Climate Zone | Zone 5 (Burlington) |  |  | 15.4 | N | ⁰F | Average temperature difference [⁰F] during heating season between outdoor air temperature and assumed 55⁰F heating base temperature
|  |  | Zone 6 (Mason City) |  |  | 24.9
|  |  | Average/Unknown |  |  | 19.1
| [3,142] |  |  |  |  | 3142 | N | Btu to kWh | Conversion from Btu to kWh.
| [η_heating_elec] | [5 empty] | Y |  | Efficiency of electric heating system
| [∆Therms] | [5 empty] | C | Therms | Gas savings calcualted with equation below
| [Fe] |  |  |  |  | 3.14% | N |  | Furnace Fan energy consumption as a percentage of annual fuel consumption
| [29.3] |  |  |  |  | 29.3 | N | kWh per therm | kWh per therm
| [CF] | Building Type | Convenience |  |  | 92.3% | N |  | Summer System Peak Coincidence Factor for Cooling (dependent on building type)
|  |  | Education |  |  | 96.7%
|  |  | Grocery |  |  | 100%
|  |  | Health |  |  | 100%
|  |  | Hospital |  |  | 98.6%
|  |  | Industrial |  |  | 44.6%
|  |  | Lodging |  |  | 97.4%
|  |  | Multifamily |  |  | 100%
|  |  | Office - Large |  |  | 98.8%
|  |  | Office - Small |  |  | 100%
|  |  | Religious |  |  | 94.3%
|  |  | Restaurant |  |  | 99.6%
|  |  | Retail - Large |  |  | 87.6%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 77.9%
|  |  | Nonresidential Average |  |  | 92.3%
| [100,000] |  |  |  |  | 100000 | N | Btu to therms | Btu to therms conversion factor
| [η_heating_gas] | [5 empty] | Y |  | Efficiency of has heating system
| [Δtherms] | [5 empty] | C | therms | Natural gas energy savings, calculated above
| [GCF] | Building Type | Convenience |  |  | 0.016482 | N |  | Gas Coincidence Factor for Heating
|  |  | Education |  |  | 0.01148
|  |  | Grocery |  |  | 0.013083
|  |  | Health |  |  | 0.010179
|  |  | Hospital |  |  | 0.015543
|  |  | Industrial |  |  | 0.014296
|  |  | Lodging |  |  | 0.013205
|  |  | Multifamily |  |  | 0.012268
|  |  | Office - Large |  |  | 0.013082
|  |  | Office - Small |  |  | 0.016718
|  |  | Religious |  |  | 0.011964
|  |  | Restaurant |  |  | 0.015262
|  |  | Retail - Large |  |  | 0.013281
|  |  | Retail - Small |  |  | 0.014055
|  |  | Warehouse |  |  | 0.015677
|  |  | Nonresidential Average |  |  | 0.014658

## Efficient Windows
Efficient Windows
| Measure Code: | NR-SHL-WIND-V05-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
20
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
$1.50/ft2
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [∆kWhcooling] + [∆kWhheating]
| Time of Sale Demand (ΔkW) | = ([∆kWhcooling] / [LHcooling]) * [CF]
| Time of Sale Gas (ΔTherms) | = (([U_code] - [U_eff]) * [A_window] * [LH_heating]* [∆T_AVG,heating])) / (([100000] * [η_heating_gas]))
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [∆kWh_cooling] |  |  | = (([U_code] - [U_eff ]) * [A_window] * [LH_cooling] * [∆T_AVG,cooling])) / (([1,000] * [η_cooling]))
| [∆kWh_heating] | Fuel Type | Electric (resistance or heat pump) | = (([U_code] - [U_eff]) * [A_window] * [LH_heating]* [∆T_AVG,heating])) / (([3,412] * [η_heating_elec]))
|  |  | Gas | = [∆Therms] * [Fe] * [29.3]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Ucode] | Climate Zone | 5 | Window Type | Fixed | 0.38 | N | Btu/ft2.°F.h | U-factor value of code baseline window assembly (Btu/ft2.°F.h)
[5 empty] | Openable | 0.45
|  |  | 6 |  | Fixed | 0.36
[5 empty] | Openable | 0.43
| [Ueff] | [5 empty] | Y | Btu/ft2.°F.h | U-factor value of the efficient window assembly (Btu/ft2.°F.h)
| [Awindow] | [5 empty] | Y | ft2 | Area of insulated window (including visible frame and glass) (ft2)
| [LHCool] | Building Type | Convenience | Climate Zone | Zone 5 (Burlington) | 3005 | N | Hours | Load Hours for cooling
|  |  | Education |  |  | 3354
|  |  | Grocery |  |  | 2871
|  |  | Health |  |  | 5240
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 3537
|  |  | Lodging |  |  | 8019
|  |  | Multifamily |  |  | 5424
|  |  | Office - Large |  |  | 4844
|  |  | Office - Small |  |  | 3941
|  |  | Religious |  |  | 4347
|  |  | Restaurant |  |  | 3019
|  |  | Retail - Large |  |  | 3621
|  |  | Retail - Small |  |  | 2636
|  |  | Warehouse |  |  | 3617
|  |  | Nonresidential Average |  |  | 3643
|  |  | Convenience |  | Zone 6 (Mason City) | 4054
|  |  | Education |  |  | 2771
|  |  | Grocery |  |  | 2425
|  |  | Health |  |  | 4405
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 4526
|  |  | Lodging |  |  | 7309
|  |  | Multifamily |  |  | 4575
|  |  | Office - Large |  |  | 4457
|  |  | Office - Small |  |  | 3265
|  |  | Religious |  |  | 5267
|  |  | Restaurant |  |  | 2217
|  |  | Retail - Large |  |  | 4623
|  |  | Retail - Small |  |  | 1839
|  |  | Warehouse |  |  | 4553
|  |  | Nonresidential Average |  |  | 3732
|  |  | Convenience |  | Average/Unknown | 3628
|  |  | Education |  |  | 2996
|  |  | Grocery |  |  | 2725
|  |  | Health |  |  | 4770
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 3977
|  |  | Lodging |  |  | 7909
|  |  | Multifamily |  |  | 5084
|  |  | Office - Large |  |  | 4596
|  |  | Office - Small |  |  | 3678
|  |  | Religious |  |  | 4763
|  |  | Restaurant |  |  | 2798
|  |  | Retail - Large |  |  | 4218
|  |  | Retail - Small |  |  | 2445
|  |  | Warehouse |  |  | 4100
|  |  | Nonresidential Average |  |  | 3734
| [ΔTAVG,cooling] | Climate Zone | Zone 5 (Burlington) |  |  | 5.4 | N | ⁰F | Average temperature difference [⁰F] during cooling season between outdoor air temperature and assumed 75⁰F indoor air temperature
|  |  | Zone 6 (Mason City) |  |  | 0.2
|  |  | Average/Unknown |  |  | 3.6
| [1,000] |  |  |  |  | 1000 | N | Btu to kBtu | Btu to kBtu conversion factor
| [ηcooling] | [5 empty] | Y | kBtu/kWh | Energy efficiency ratio (EER) of cooling system (kBtu/kWh)
| [LHHeat] | Building Type | Convenience | Climate Zone | Zone 5 (Burlington) | 3024 | N | Hours | Load Hours for heating space
|  |  | Education |  |  | 6213
|  |  | Grocery |  |  | 6217
|  |  | Health |  |  | 8729
|  |  | Hospital |  |  | 8286
|  |  | Industrial |  |  | 3396
|  |  | Lodging |  |  | 5218
|  |  | Multifamily |  |  | 5145
|  |  | Office - Large |  |  | 5037
|  |  | Office - Small |  |  | 4641
|  |  | Religious |  |  | 2485
|  |  | Restaurant |  |  | 2954
|  |  | Retail - Large |  |  | 2699
|  |  | Retail - Small |  |  | 4222
|  |  | Warehouse |  |  | 2025
|  |  | Nonresidential Average |  |  | 3480
|  |  | Convenience |  | Zone 6 (Mason City) | 2129
|  |  | Education |  |  | 6633
|  |  | Grocery |  |  | 6819
|  |  | Health |  |  | 8732
|  |  | Hospital |  |  | 8272
|  |  | Industrial |  |  | 2233
|  |  | Lodging |  |  | 6234
|  |  | Multifamily |  |  | 5998
|  |  | Office - Large |  |  | 5787
|  |  | Office - Small |  |  | 5329
|  |  | Religious |  |  | 1667
|  |  | Restaurant |  |  | 3619
|  |  | Retail - Large |  |  | 1807
|  |  | Retail - Small |  |  | 4935
|  |  | Warehouse |  |  | 1390
|  |  | Nonresidential Average |  |  | 3473
|  |  | Convenience |  | Average/Unknown | 2690
|  |  | Education |  |  | 6430
|  |  | Grocery |  |  | 6499
|  |  | Health |  |  | 8720
|  |  | Hospital |  |  | 8289
|  |  | Industrial |  |  | 3080
|  |  | Lodging |  |  | 5500
|  |  | Multifamily |  |  | 5382
|  |  | Office - Large |  |  | 5316
|  |  | Office - Small |  |  | 5087
|  |  | Religious |  |  | 2223
|  |  | Restaurant |  |  | 3321
|  |  | Retail - Large |  |  | 2405
|  |  | Retail - Small |  |  | 4596
|  |  | Warehouse |  |  | 1788
|  |  | Nonresidential Average |  |  | 3561
| [ΔTAVG,heating] | Climate Zone | Zone 5 (Burlington) |  |  | 15.4 | N | ⁰F | Average temperature difference [⁰F] during heating season between outdoor air temperature and assumed 55⁰F heating base temperature
|  |  | Zone 6 (Mason City) |  |  | 24.9
|  |  | Average/Unknown |  |  | 19.1
| [3,142] |  |  |  |  | 3142 | N | Btu to kWh | Conversion from Btu to kWh.
| [η_heating_elec] | [5 empty] | Y |  | Efficiency of electric heating system
| [∆Therms] | [5 empty] | C | Therms | Gas savings calcualted with equation below
| [Fe] |  |  |  |  | 3.14% | N |  | Furnace Fan energy consumption as a percentage of annual fuel consumption
| [29.3] |  |  |  |  | 29.3 | N | kWh per therm | kWh per therm
| [CF] | Building Type | Convenience |  |  | 92.3% | N |  | Summer System Peak Coincidence Factor for Cooling (dependent on building type)
|  |  | Education |  |  | 96.7%
|  |  | Grocery |  |  | 100%
|  |  | Health |  |  | 100%
|  |  | Hospital |  |  | 98.6%
|  |  | Industrial |  |  | 44.6%
|  |  | Lodging |  |  | 97.4%
|  |  | Multifamily |  |  | 100%
|  |  | Office - Large |  |  | 98.8%
|  |  | Office - Small |  |  | 100%
|  |  | Religious |  |  | 94.3%
|  |  | Restaurant |  |  | 99.6%
|  |  | Retail - Large |  |  | 87.6%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 77.9%
|  |  | Nonresidential Average |  |  | 92.3%
| [100,000] |  |  |  |  | 100000 | N | Btu to therms | Btu to therms conversion factor
| [η_heating_gas] | [5 empty] | Y |  | Efficiency of has heating system
| [Δtherms] | [5 empty] | C | therms | Natural gas energy savings, calculated above
| [GCF] | Building Type | Convenience |  |  | 0.016482 | N |  | Gas Coincidence Factor for Heating
|  |  | Education |  |  | 0.01148
|  |  | Grocery |  |  | 0.013083
|  |  | Health |  |  | 0.010179
|  |  | Hospital |  |  | 0.015543
|  |  | Industrial |  |  | 0.014296
|  |  | Lodging |  |  | 0.013205
|  |  | Multifamily |  |  | 0.012268
|  |  | Office - Large |  |  | 0.013082
|  |  | Office - Small |  |  | 0.016718
|  |  | Religious |  |  | 0.011964
|  |  | Restaurant |  |  | 0.015262
|  |  | Retail - Large |  |  | 0.013281
|  |  | Retail - Small |  |  | 0.014055
|  |  | Warehouse |  |  | 0.015677
|  |  | Nonresidential Average |  |  | 0.014658

## Insulated Doors
Insulated Doors
| Measure Code: | NR-SHL-DOOR-V05-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
25
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [∆kWhcooling] + [∆kWhheating]
| Time of Sale Demand (ΔkW) | = ([∆kWhcooling] / [LHcooling]) * [CF]
| Time of Sale Gas (ΔTherms) | = ((1 / [R_existing] - 1 / [R_new]) * [Area] * [LH_heating] * [∆T_AVG,heating]) / ([100,000] * [η_heat_gas])
| Time of Sale Peak Gas (ΔPeakTherms) | = [Δtherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [∆kWh_cooling] |  |  | = ((1 / [R_existing] - 1 / [R_new]) *[ Area] * [LH_cooling] * [∆T_AVG,cooling]) / (([1,000] * [η_cooling]))
| [∆kWh_heating] | Fuel Type | Electric (resistance or heat pump) | = ((1 / [R_existing] - 1 / [R_new]) * [Area]) * [LH_heating] * [∆T_AVG,heating]) / ([3,412] * [η_heating_elec])
|  |  | Gas | = [∆Therms] * [Fe] * [29.3]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Rexisting] | Door Type | Swinging |  |  | 2.7 | Y | (['hr-⁰F-ft2)/Btu | Existing door heat loss coefficient [(hr-⁰F-ft2)/Btu].
|  |  | Nonswinging |  |  | 4.75
| [Rnew] | [5 empty] | Y | (['hr-⁰F-ft2)/Btu | New door heat loss coefficient [(hr-⁰F-ft2)/Btu]
| [Area] | [5 empty] | Y | ft2 | Area of the door surface in square feet.
| [LHCool] | Building Type | Convenience | Climate Zone | Zone 5 (Burlington) | 3005 | N | Hours | Load Hours for cooling
|  |  | Education |  |  | 3354
|  |  | Grocery |  |  | 2871
|  |  | Health |  |  | 5240
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 3537
|  |  | Lodging |  |  | 8019
|  |  | Multifamily |  |  | 5424
|  |  | Office - Large |  |  | 4844
|  |  | Office - Small |  |  | 3941
|  |  | Religious |  |  | 4347
|  |  | Restaurant |  |  | 3019
|  |  | Retail - Large |  |  | 3621
|  |  | Retail - Small |  |  | 2636
|  |  | Warehouse |  |  | 3617
|  |  | Nonresidential Average |  |  | 3643
|  |  | Convenience |  | Zone 6 (Mason City) | 4054
|  |  | Education |  |  | 2771
|  |  | Grocery |  |  | 2425
|  |  | Health |  |  | 4405
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 4526
|  |  | Lodging |  |  | 7309
|  |  | Multifamily |  |  | 4575
|  |  | Office - Large |  |  | 4457
|  |  | Office - Small |  |  | 3265
|  |  | Religious |  |  | 5267
|  |  | Restaurant |  |  | 2217
|  |  | Retail - Large |  |  | 4623
|  |  | Retail - Small |  |  | 1839
|  |  | Warehouse |  |  | 4553
|  |  | Nonresidential Average |  |  | 3732
|  |  | Convenience |  | Average/Unknown | 3628
|  |  | Education |  |  | 2996
|  |  | Grocery |  |  | 2725
|  |  | Health |  |  | 4770
|  |  | Hospital |  |  | 8760
|  |  | Industrial |  |  | 3977
|  |  | Lodging |  |  | 7909
|  |  | Multifamily |  |  | 5084
|  |  | Office - Large |  |  | 4596
|  |  | Office - Small |  |  | 3678
|  |  | Religious |  |  | 4763
|  |  | Restaurant |  |  | 2798
|  |  | Retail - Large |  |  | 4218
|  |  | Retail - Small |  |  | 2445
|  |  | Warehouse |  |  | 4100
|  |  | Nonresidential Average |  |  | 3734
| [ΔTAVG,cooling] | Climate Zone | Zone 5 (Burlington) |  |  | 5.4 | N | ⁰F | Average temperature difference [⁰F] during cooling season between outdoor air temperature and assumed 75⁰F indoor air temperature
|  |  | Zone 6 (Mason City) |  |  | 0.2
|  |  | Average/Unknown |  |  | 3.6
| [1,000] |  |  |  |  | 1000 | N | Btu to kBtu | Btu to kBtu conversion factor
| [ηcooling] | [5 empty] | Y | kBtu/kWh | Seasonal energy efficiency ratio (SEER) of cooling system (kBtu/kWh)
| [LHHeat] | Building Type | Convenience | Climate Zone | Zone 5 (Burlington) | 3024 | N | Hours | Load Hours for heating space
|  |  | Education |  |  | 6213
|  |  | Grocery |  |  | 6217
|  |  | Health |  |  | 8729
|  |  | Hospital |  |  | 8286
|  |  | Industrial |  |  | 3396
|  |  | Lodging |  |  | 5218
|  |  | Multifamily |  |  | 5145
|  |  | Office - Large |  |  | 5037
|  |  | Office - Small |  |  | 4641
|  |  | Religious |  |  | 2485
|  |  | Restaurant |  |  | 2954
|  |  | Retail - Large |  |  | 2699
|  |  | Retail - Small |  |  | 4222
|  |  | Warehouse |  |  | 2025
|  |  | Nonresidential Average |  |  | 3480
|  |  | Convenience |  | Zone 6 (Mason City) | 2129
|  |  | Education |  |  | 6633
|  |  | Grocery |  |  | 6819
|  |  | Health |  |  | 8732
|  |  | Hospital |  |  | 8272
|  |  | Industrial |  |  | 2233
|  |  | Lodging |  |  | 6234
|  |  | Multifamily |  |  | 5998
|  |  | Office - Large |  |  | 5787
|  |  | Office - Small |  |  | 5329
|  |  | Religious |  |  | 1667
|  |  | Restaurant |  |  | 3619
|  |  | Retail - Large |  |  | 1807
|  |  | Retail - Small |  |  | 4935
|  |  | Warehouse |  |  | 1390
|  |  | Nonresidential Average |  |  | 3473
|  |  | Convenience |  | Average/Unknown | 2690
|  |  | Education |  |  | 6430
|  |  | Grocery |  |  | 6499
|  |  | Health |  |  | 8720
|  |  | Hospital |  |  | 8289
|  |  | Industrial |  |  | 3080
|  |  | Lodging |  |  | 5500
|  |  | Multifamily |  |  | 5382
|  |  | Office - Large |  |  | 5316
|  |  | Office - Small |  |  | 5087
|  |  | Religious |  |  | 2223
|  |  | Restaurant |  |  | 3321
|  |  | Retail - Large |  |  | 2405
|  |  | Retail - Small |  |  | 4596
|  |  | Warehouse |  |  | 1788
|  |  | Nonresidential Average |  |  | 3561
| [ΔTAVG,heating] | Climate Zone | Zone 5 (Burlington) |  |  | 15.4 | N | ⁰F | Average temperature difference [⁰F] during heating season between outdoor air temperature and assumed 55⁰F heating base temperature
|  |  | Zone 6 (Mason City) |  |  | 24.9
|  |  | Average/Unknown |  |  | 19.1
| [3,142] |  |  |  |  | 3142 | N | Btu to kWh | Conversion from Btu to kWh.
| [η_heating_elec] | [5 empty] | Y |  | Efficiency of electric heating system
| [∆Therms] | [5 empty] | C | Therms | Gas savings calcualted with equation below
| [Fe] |  |  |  |  | 3.14% | N |  | Furnace Fan energy consumption as a percentage of annual fuel consumption
| [29.3] |  |  |  |  | 29.3 | N | kWh per therm | kWh per therm
| [CF] | Building Type | Convenience |  |  | 92.3% | N |  | Summer System Peak Coincidence Factor for Cooling (dependent on building type)
|  |  | Education |  |  | 96.7%
|  |  | Grocery |  |  | 100%
|  |  | Health |  |  | 100%
|  |  | Hospital |  |  | 98.6%
|  |  | Industrial |  |  | 44.6%
|  |  | Lodging |  |  | 97.4%
|  |  | Multifamily |  |  | 100%
|  |  | Office - Large |  |  | 98.8%
|  |  | Office - Small |  |  | 100%
|  |  | Religious |  |  | 94.3%
|  |  | Restaurant |  |  | 99.6%
|  |  | Retail - Large |  |  | 87.6%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 77.9%
|  |  | Nonresidential Average |  |  | 92.3%
| [100,000] |  |  |  |  | 100000 | N | Btu to therms | Btu to therms conversion factor
| [η_heating_gas] | [5 empty] | Y |  | Efficiency of has heating system
| [Δtherms] | [5 empty] | C | therms | Natural gas energy savings, calculated above
| [GCF] | Building Type | Convenience |  |  | 0.016482 | N |  | Gas Coincidence Factor for Heating
|  |  | Education |  |  | 0.01148
|  |  | Grocery |  |  | 0.013083
|  |  | Health |  |  | 0.010179
|  |  | Hospital |  |  | 0.015543
|  |  | Industrial |  |  | 0.014296
|  |  | Lodging |  |  | 0.013205
|  |  | Multifamily |  |  | 0.012268
|  |  | Office - Large |  |  | 0.013082
|  |  | Office - Small |  |  | 0.016718
|  |  | Religious |  |  | 0.011964
|  |  | Restaurant |  |  | 0.015262
|  |  | Retail - Large |  |  | 0.013281
|  |  | Retail - Small |  |  | 0.014055
|  |  | Warehouse |  |  | 0.015677
|  |  | Nonresidential Average |  |  | 0.014658

## LED Fridge Case Light Oc Sensor
LED Refrigerator Case Light Occupancy Sensor
| Measure Code: | NR-RFG-CLOS-V01-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
8
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost | Known |  | Actual
|  | Unknown |  | 60
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =[kW_Controlled] * ([Hours] * [%Controlled]) * ( 1 + ([0.80] / [COP]))
| Time of Sale Demand (ΔkW) | =([∆kWh] / [Hours]) * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [ΔkWh] | Type | Cooler |  |  | 290.8 | C | kWh | Savings per control. Deemed values provided or use algorithm.
|  |  | Freezer |  |  | 331.4
| [kWControlled] |  |  |  |  | 0.09 | Y | kW | Total lighting load (kW) connected to the control.
| [Hours] |  |  |  |  | 6575 | Y | hours | Annual case lighting hours of use
| [%Controlled] |  |  |  |  | 40% | Y |  | Percentage savings due to the occupancy sensor
| [0.80] |  |  |  |  | 0.8 | N |  | Percentage of heat from LED lighting assumed to be transferred to the refrigeration system
| [COP] | Type | Cooler |  |  | 3.5 | Y |  | Coefficient of performance of cooler or freezer
|  |  | Freezer |  |  | 2
| [CF] |  |  |  |  | 1 | N |  | Summer peak coincidence factor

## Door Heater Ctrl Cool Freezer
Door Heater Controls for Cooler or Freezer
| Measure Code: | NR-RFG-DHCT-V02-180101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
12
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known |  | Actual
|  | Unknown |  | $1266 / heater control
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =[DoorFt] × ([kW_Base] / [DoorFt] × [Hours] × [%Off] × (1 + [R_H] / [COP]))
| Time of Sale Demand (ΔkW) | =([∆kWh] / [Hours]) * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [ΔkWh] | Type | Cooler |  |  | 838.4 | C | kWh | Savings per control. Deemed values provided or use algorithm.
|  |  | Freezer |  |  | 1020.5
| [kWBase] | Type | Cooler |  |  | 0.109 | Y | kW | Per door electric energy consumption of door heater without controls
|  |  | Freezer |  |  | 0.191
| [DoorFt] |  |  |  |  | 2.5 | Y | ft | Door length in liner feet
| [Hours] |  |  |  |  | 8776 | Y | Hours | Annual hours of cooler or freezer operation
| [%Off] | Type | Cooler |  |  | 74% | Y |  | Percentage of hours annually that the door heater is powered off due to controls
|  |  | Freezer |  |  | 46%
| [RH] |  |  |  |  | 0.65 | Y |  | Residual heat fraction: estimated percentage of heat produced by heaters that remains in the freezer or cooler case and must be removed by the refrigeration unit
| [COP] | Type | Cooler |  |  | 3.5 | Y |  | Coeffiecint of performance of cooler or freezer
|  |  | Freezer |  |  | 2
| [CF] |  |  |  |  | 0.964 | N |  | Summer peak coincidence factor

## Eff Motors Walk-in Display
Efficient Motors for Walk-in and Display Case Coolers/Freezers
| Measure Code: | NR-RFG-ECMF-V03-190101
| Lifetime of Efficient Equipment: | [6 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known |  |  |  | Actual
|  | Unknown | Motor type | ECM |  | 245
|  |  |  | Q-Sync |  | 170
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([W_Output] / [EFF_Base] - [W_Output] / [EFF_ECM]) / [1,000] × [Hours] × [DC] × [LF] × (1 + 1 / [COP])
| Time of Sale Demand (ΔkW) | =([∆kWh] / [Hours]) * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Dependent Variable Input 3 | Dependent Variable 3 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [ΔkWh] | Refrigeration Type | Cooler | Application | Display Case | Installed Motor Type | ECM | 293.1 | C | kWh | Savings per motor. Deemed values provided or use algorithm.
[7 empty] | Q-Sync | 315.5
[5 empty] | Walk-in |  | ECM | 823.6
[7 empty] | Q-Sync | 886.3
|  |  | Freezer |  | Display Case |  | ECM | 321.5
[7 empty] | Q-Sync | 346
[5 empty] | Walk-in |  | ECM | 903.2
[7 empty] | Q-Sync | 971.9
| [Woutput] | Application | Display Case |  |  |  |  | 14.95 | Y | W | Output wattage of installed fan motor
|  |  | Walk-in |  |  |  |  | 42
| [EFFBase] | [6 empty] | 29% | Y |  | Efficiency of baseline motor
| [EFFEE] | Motor type | ECM |  |  |  |  | 66% | Y |  | Efficiency of efficient motor
|  |  | Q-sync |  |  |  |  | 73.1%
| [1000] | [6 empty] | 1000 | N | W to kW | Conversion factor from watts to kilowatts
| [Hours] | [6 empty] | 8766 | N | Hours | Annual hours of cooler or freezer operation
| [LF] | [6 empty] | 0.9 | Y |  | Load factor of fan motor
| [DC] | Refrigeration Type | Cooler |  |  |  |  | 100% | Y |  | Duty cycle of fan motor
|  |  | Freezer |  |  |  |  | 94%
| [COP] | Refrigeration Type | Cooler |  |  |  |  | 3.5 | N |  | Coefficient of performance of cooler or freezer
|  |  | Freezer |  |  |  |  | 2
| [CF] | [6 empty] | 0.964 | N |  | Summer peak coincidence factor

## Night Covers
Night Covers for Open Refrigerated Display Cases
| Measure Code: | NR-RFG-NCOV-V02-180101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
5
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known |  | Actual
|  | Unknown |  | $42 per linear foot
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =[CaseFt] * [SavingsRate] * [Hours] * [Days]
Time of Sale Demand (ΔkW)
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [CaseFt] | [5 empty] | Y | ft | Width (ft) of the case opening projected by night cover
| [SavingsRate] | Display Case Temperature | Low (-35 to -5) |  |  | 0.03 | Y | kWh/ft | Electric demand savings (kW/ft) from installing a night cover
|  |  | Medium (0 to 30) |  |  | 0.02
|  |  | High (35 to 55) |  |  | 0.01
| [Hours] |  |  |  |  | 6 | Y | Hours | Number of hours per day that the night covers are in use
| [Days] |  |  |  |  | 365.25 | Y | Days | Number of days per year that the night covers are in use

## Refrigerated Bev Vend Machine
Refrigerated Beverage Vending Machine
| Measure Code: | NR-RFG-ESVE-V03-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
10
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
199
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =([kWh_Base] - [kWh_ESTAR])* [Days]
| Time of Sale Demand (ΔkW) | =([∆kWh] / [Hours]) * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [kWhBase] | Equipment Type | Class A | = 0.052 * [V] + 2.43
|  |  | Class B | = 0.052 * [V] + 2.20
|  |  | Combination A | = 0.086 * [V] + 2.66
|  |  | Combination B | = 0.111 * [V] + 2.04
| [kWhESTAR] | Equipment Type | Class A | = 0.04836 * [V] + 2.2599
|  |  | Class B | = 0.04576 * [V] + 1.936
|  |  | Combination A | = 0.07998 * [V] + 2.4738
|  |  | Combination B | = 0.09768 * [V] + 1.7952
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [kWhBase] | [5 empty] | C | Volume | Maximum daily energy consumption (kWh/day) of baseline vending machine
| [kWhESTAR] |  |  |  |  | Actual | C | Volume | Maximum daily energy consumption (kWh/day) of ENERGY STAR vending machine. Actual or use algorithm
| [V] | [5 empty] | Y | ft3 | Refrigerated volume (ft3)
| [Days] |  |  |  |  | 365.25 | N | Days | Days of vending machine operation per year
| [ΔkWh] | [5 empty] | C | kWh | Electric energy savings, calculated above
| [Hours] |  |  |  |  | 8766 | N | Hours | Hours of vending machine operation per year
| [CF] |  |  |  |  | 0.964 | N |  | Summer peak coincidence factor

## Fridge Recycling - Regression
Fridge Recycling - Regression
| Measure Code: | NR-REF-RFRC-V02-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
6.5
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Program Cost | Known | Actual
|  | Unknown | 120
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =[∆kWh_Unit]+([∆kWh_Unit]*([WHFeHeatElectric] + [WHFeCool]))
| Time of Sale Demand (ΔkW) | = ([∆kWh_Unit])/([HOURS] ) * [WHFdCool]* [CF]
| Time of Sale Gas (ΔTherms) | =[∆kWh_Unit]*[WHFeHeatGas]* [0.03412]
| Time of Sale Peak Gas (ΔPeakTherms) | =(([ΔTherms]))/[HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [kWh_Unit] |  |  | = (83.32 + ([Age] * 3.68) + ([Pre-1990] * 485.04) + ([Size] * 27.15) + ([Side-by-side] * 406.78) + ([Primary Usage] * 161.86) + ([CDD]/365.25 * [unconditioned] * 15.37) + ([HDD]/365.25 *[unconditioned] *-11.07)] - [UEC_BaseRefrig]
| [WHFeHeatElectric] |  |  | = - ([HF] / [ηHeatElectric]) * [%ElecHeat]
| [WHFeCool] |  |  | = ([CoolF] / [ηCool]) * [%Cool]
| [WHFeHeatGas] |  |  | = - ([HF] /[ηHeatGas]) * [%GasHeat]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [∆kWh_Unit] | [5 empty] | C | kWh | Unit energy savings
| [Age] | [5 empty] | Y | Years | Age of retired unit
| [Pre-1990] | Manufacture Year | Pre-1990 |  |  | 1 | N |  | Pre-1990 dummy
|  |  | Post-1990 |  |  | 0
| [Size] | [5 empty] | C | ft3 | Capacity (cubmic feet) of retired unit
| [Side-by-side] | Type | Side-by-side |  |  | 1 | N |  | Side-by-side dummy
|  |  | Other |  |  | 0
| [Primary Usage] | Usage | Primary |  |  | 1 | N |  | Primary Usage Type (in absence of the program) dummy
|  |  | Not Primary |  |  | 0
| [CDD] | Location | 5 (Burlington) |  |  | 1209 | N | Days | Cooling Degree Days
|  |  | 6 (Mason City) |  |  | 616
|  |  | Average/unknown |  |  | 1068
| [Unconditioned] | Location | Unconditioned space |  |  | 1 | N |  | If unit in unconditioned space = 1, otherwise 0
|  |  | Conditioned space |  |  | 0
| [HDD] | Location | 5 (Burlington) |  |  | 4496 | N | Days | Heating Degree Days
|  |  | 6 (Mason City) |  |  | 6391
|  |  | Average/unknown |  |  | 5052
| [UEC_BaseRefrig] |  |  |  |  | 592 | N | kWh | Assumed consumption of a new baseline residential-sized refrigerator
| [WHFeHeatElectric] | [5 empty] | C |  | Waste Heat Factor for Energy to account for electric heating increase from removing waste heat from refrigerator/freezer (if fossil fuel heating – see calculation of heating penalty in that section).
| [HF] | Location | Heated Space |  |  | 54% | N |  | Heating factor or percentage of reduced waste heat that must now be heated
|  |  | Heated Space or Unknown |  |  | 0%
| [ηHeatElectric] | System Type | Heat Pump | Age of Equipment | Before 2006 | 2 | Y | COP | Efficiency in COP of Heating equipment
[5 empty] | 2006-2014 | 2.26
[5 empty] | 2015 on | 2.4
|  |  | Resistance |  |  | 1
|  |  | Unknown |  |  | 1.38
| [%ElecHeat] | Heating Fuel | Electric |  |  | 100% | N | % | Percentage of home with electric heat
|  |  | Fosil Fuel |  |  | 0%
|  |  | Unknown |  |  | 30%
| [WHFeCool] | [5 empty] | C |  | Waste Heat Factor for Energy to account for cooling savings from removing waste heat from refrigerator/freezer.
| [CoolF] | Cooling of Space | Cooling |  |  | 34% | N | % | Cooling Factor or percentage of reduced waste heat that no longer needs to be cooled
|  |  | No Cooling |  |  | 0%
| [ηCool] |  |  |  |  | 2.8 | Y | COP | Efficiency in COP of Cooling equipment
| [%Cool] | Cooling of Space | Cooling |  |  | 100% | N | % | Percentage of home with cooling
|  |  | No Cooling |  |  | 0%
|  |  | Unknown |  |  | 74%
| [Hours] |  |  |  |  | 5280 | N |  | Equivalent Full Load Hours as calculated using eShapes loadprofile
| [WHFdCool] | Location | Cooled space |  |  | 1.29 | N |  | Waste heat factor for demand to account for cooling savings from removing waste heat.
|  |  | Uncooled space |  |  | 1
|  |  | Unknown space |  |  | 1.21
| [CF] |  |  |  |  | 70.9% | N |  | Coincident factor as calculated using eShapes loadprofile
| [WHFeHeatGas] | [5 empty] | C |  | Waste Heat Factor for Energy to account for gas heating increase from removing waste heat from refrigerator/freezer
| [ηHeatGas ] |  |  |  |  | 74% | N |  | Efficiency of heating system
| [%GasHeat] | Fuel Type | Electric |  |  | 0% | N |  | Percentage of homes with gas heat
|  |  | Gas |  |  | 100%
|  |  | Unknown |  |  | 70%
| [0.03412] |  |  |  |  | 0.03412 | N | kWh to Therms | Converts kWh to Therms
| [ΔTherms] | [5 empty] | C | Therms | Therm impact calcualted aboce
| [HeatDays] |  |  |  |  | 197 | N | Days | Heat season days per year

## Fridge Recycling - Deemed
Fridge Recycling - Deemed
| Measure Code: | NR-REF-RFRC-V02-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime (years) |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime (years)
6.5
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Program Cost Known | Known | Actual
|  | Unknown | 120
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =[∆kWh_Unit]+([∆kWh_Unit]*([WHFeHeatElectric] + [WHFeCool]))
| Time of Sale Demand (ΔkW) | = ([∆kWh_Unit])/([HOURS] ) * [WHFdCool]* [CF]
| Time of Sale Gas (ΔTherms) | =[∆kWh_Unit]*[WHFeHeatGas]* [0.03412]
| Time of Sale Peak Gas (ΔPeakTherms) | =(([ΔTherms]))/[HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWh_Unit] |  |  | = [UEC_Retired] - [UEC_BaseRefrig]
| [WHFeHeatElectric] |  |  | = - ([HF] / [ηHeatElectric]) * [%ElecHeat]
| [WHFeCool] |  |  | = ([CoolF] / [ηCool]) * [%Cool]
| [WHFeHeatGas] |  |  | = - ([HF] /[ηHeatGas]) * [%GasHeat]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [∆kWh_Unit] |  |  |  |  | 440 | C | kWh | Unit energy savings
| [UEC] |  |  |  |  | 1032 | N | kWh | Unit Energy Consumption
| [UEC_BaseRefrig] |  |  |  |  | 592 | N | kWh | Assumed consumption of a new baseline residential-sized refrigerator
| [WHFeHeatElectric] | [5 empty] | C |  | Waste Heat Factor for Energy to account for electric heating increase from removing waste heat from refrigerator/freezer (if fossil fuel heating – see calculation of heating penalty in that section).
| [HF] | Location | Heated Space |  |  | 54% | N |  | Heating factor or percentage of reduced waste heat that must now be heated
|  |  | Heated Space or Unknown |  |  | 0%
| [ηHeatElectric] | System Type | Heat Pump | Age of Equipment | Before 2006 | 2 | Y | COP | Efficiency in COP of Heating equipment
[5 empty] | 2006-2014 | 2.26
[5 empty] | 2015 on | 2.4
|  |  | Resistance |  |  | 1
|  |  | Unknown |  |  | 1.38
| [%ElecHeat] | Heating Fuel | Electric |  |  | 100% | N | % | Percentage of home with electric heat
|  |  | Fosil Fuel |  |  | 0%
|  |  | Unknown |  |  | 30%
| [WHFeCool] | [5 empty] | C |  | Waste Heat Factor for Energy to account for cooling savings from removing waste heat from refrigerator/freezer.
| [CoolF] | Cooling of Space | Cooling |  |  | 34% | N | % | Cooling Factor or percentage of reduced waste heat that no longer needs to be cooled
|  |  | No Cooling |  |  | 0%
| [ηCool] |  |  |  |  | 2.8 | Y | COP | Efficiency in COP of Cooling equipment
| [%Cool] | Cooling of Space | Cooling |  |  | 100% | N | % | Percentage of home with cooling
|  |  | No Cooling |  |  | 0%
|  |  | Unknown |  |  | 74%
| [ΔkW] |  |  |  |  | 0.0715 | C | kW | Deemed approach; Refrigerators
| [Hours] |  |  |  |  | 5280 | N |  | Equivalent Full Load Hours as calculated using eShapes loadprofile
| [WHFdCool] | Location | Cooled space |  |  | 1.29 | N |  | Waste heat factor for demand to account for cooling savings from removing waste heat.
|  |  | Uncooled space |  |  | 1
|  |  | Unknown space |  |  | 1.21
| [CF] |  |  |  |  | 70.9% | N |  | Coincident factor as calculated using eShapes loadprofile
| [WHFeHeatGas] | [5 empty] | C |  | Waste Heat Factor for Energy to account for gas heating increase from removing waste heat from refrigerator/freezer
| [ηHeatGas ] |  |  |  |  | 74% | N |  | Efficiency of heating system
| [%GasHeat] | Fuel Type | Electric |  |  | 0% | N |  | Percentage of homes with gas heat
|  |  | Gas |  |  | 100%
|  |  | Unknown |  |  | 70%
| [0.03412] |  |  |  |  | 0.03412 | N | kWh to Therms | Converts kWh to Therms
| [ΔTherms] | [5 empty] | C | Therms | Therm impact calcualted aboce
| [HeatDays] |  |  |  |  | 197 | N | Days | Heat season days per year

## Freezer Recycling - Regression
Freezer Recycling - Regression
| Measure Code: | NR-REF-RFRC-V02-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
6.5
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Program Cost | Known | Actual
|  | Unknown | 120
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =[∆kWh_Unit]+([∆kWh_Unit]*([WHFeHeatElectric] + [WHFeCool]))
| Time of Sale Demand (ΔkW) | =[∆kWh_Unit]/([HOURS] ) *[WHFdCool]* [CF]
| Time of Sale Gas (ΔTherms) | =[∆kWh_Unit]*[WHFeHeatGas]* [0.03412]
| Time of Sale Peak Gas (ΔPeakTherms) | =[ΔTherms]/[HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [kWh_Unit] |  |  | = (132.12 + ([Age] * 12.13) + ([Pre-1990] * 156.18) + ([Size] * 31.84) + ([Chest Freezer] * -19.71) + ([CDD]/365.25* [unconditioned] *9.78) + ([HDD]/365.25*[unconditioned] *-12.75)] - [UEC_BaseFreezer]
| [WHFeHeatElectric] |  |  | = - ([HF] / [ηHeatElectric]) * [%ElecHeat]
| [WHFeCool] |  |  | = ([CoolF] / [ηCool]) * [%Cool]
| [WHFeHeatGas] |  |  | = - ([HF] /[ηHeatGas]) * [%GasHeat]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [∆kWh_Unit] | [5 empty] | C | kWh | Unit energy savings
| [Age] | [5 empty] | Y | Years | Age of retired unit
| [Pre-1990] | Manufacture Year | Pre-1990 |  |  | 1 | N |  | Pre-1990 dummy
|  |  | Post-1990 |  |  | 0
| [Size] | [5 empty] | C | ft3 | Capacity (cubmic feet) of retired unit
| [Chest freezer] | Type | Chest freezer |  |  | 1 | N |  | Side-by-side dummy
|  |  | Other |  |  | 0
| [CDD] | Location | 5 (Burlington) |  |  | 1209 | N | Days | Cooling Degree Days
|  |  | 6 (Mason City) |  |  | 616
|  |  | Average/unknown |  |  | 1068
| [Unconditioned] | Location | Unconditioned space |  |  | 1 | N |  | If unit in unconditioned space = 1, otherwise 0
|  |  | Conditioned space |  |  | 0
| [HDD] | Location | 5 (Burlington) |  |  | 4496 | N | Days | Heating Degree Days
|  |  | 6 (Mason City) |  |  | 6391
|  |  | Average/unknown |  |  | 5052
| [UEC_BaseFreezer] |  |  |  |  | 381 | N | kWh | Assumed consumption of a new baseline residential-sized freezer
| [WHFeHeatElectric] | [5 empty] | C |  | Waste Heat Factor for Energy to account for electric heating increase from removing waste heat from refrigerator/freezer (if fossil fuel heating – see calculation of heating penalty in that section).
| [HF] | Location | Heated Space |  |  | 54% | N |  | Heating factor or percentage of reduced waste heat that must now be heated
|  |  | Heated Space or Unknown |  |  | 0%
| [ηHeatElectric] | System Type | Heat Pump | Age of Equipment | Before 2006 | 2 | Y | COP | Efficiency in COP of Heating equipment
[5 empty] | 2006-2014 | 2.26
[5 empty] | 2015 on | 2.4
|  |  | Resistance |  |  | 1
|  |  | Unknown |  |  | 1.38
| [%ElecHeat] | Heating Fuel | Electric |  |  | 100% | N | % | Percentage of home with electric heat
|  |  | Fosil Fuel |  |  | 0%
|  |  | Unknown |  |  | 30%
| [WHFeCool] | [5 empty] | C |  | Waste Heat Factor for Energy to account for cooling savings from removing waste heat from refrigerator/freezer.
| [CoolF] | Cooling of Space | Cooling |  |  | 34% | N | % | Cooling Factor or percentage of reduced waste heat that no longer needs to be cooled
|  |  | No Cooling |  |  | 0%
| [ηCool] |  |  |  |  | 2.8 | Y | COP | Efficiency in COP of Cooling equipment
| [%Cool] | Cooling of Space | Cooling |  |  | 100% | N | % | Percentage of home with cooling
|  |  | No Cooling |  |  | 0%
|  |  | Unknown |  |  | 74%
| [Hours] |  |  |  |  | 5895 | N |  | Equivalent Full Load Hours as calculated using eShapes loadprofile
| [WHFdCool] | Location | Cooled space |  |  | 1.29 | N |  | Waste heat factor for demand to account for cooling savings from removing waste heat.
|  |  | Uncooled space |  |  | 1
|  |  | Unknown space |  |  | 1.21
| [CF] |  |  |  |  | 95.3% | N |  | Coincident factor as calculated using eShapes loadprofile
| [WHFeHeatGas] | [5 empty] | C |  | Waste Heat Factor for Energy to account for gas heating increase from removing waste heat from refrigerator/freezer
| [ηHeatGas ] |  |  |  |  | 74% | N |  | Efficiency of heating system
| [%GasHeat] | Fuel Type | Electric |  |  | 0% | N |  | Percentage of homes with gas heat
|  |  | Gas |  |  | 100%
|  |  | Unknown |  |  | 70%
| [0.03412] |  |  |  |  | 0.03412 | N | kWh to Therms | Converts kWh to Therms
| [ΔTherms] | [5 empty] | C | Therms | Therm impact calcualted aboce
| [HeatDays] |  |  |  |  | 197 | N | Days | Heat season days per year

## Freezer Recycling - Deemed
Freezer Recycling - Deemed
| Measure Code: | NR-REF-RFRC-V02-200101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime (years) |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime (years)
6.5
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Program Cost Known | Known | Actual
|  | Unknown | 120
O&M Cost:
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =[∆kWh_Unit]+([∆kWh_Unit]*([WHFeHeatElectric] + [WHFeCool]))
| Time of Sale Demand (ΔkW) | = ([∆kWh_Unit])/([HOURS] ) * [WHFdCool]* [CF]
| Time of Sale Gas (ΔTherms) | =[∆kWh_Unit]*[WHFeHeatGas]* [0.03412]
| Time of Sale Peak Gas (ΔPeakTherms) | =(([ΔTherms]))/[HeatDays]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [ΔkWh_Unit] |  |  | = [UEC_Retired] - [UEC_BaseFreezer]
| [WHFeHeatElectric] |  |  | = - ([HF] / [ηHeatElectric]) * [%ElecHeat]
| [WHFeCool] |  |  | = ([CoolF] / [ηCool]) * [%Cool]
| [WHFeHeatGas] |  |  | = - ([HF] /[ηHeatGas]) * [%GasHeat]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [∆kWh_Unit] |  |  |  |  | 563 | C | kWh | Unit energy savings
| [UEC] |  |  |  |  | 944 | N | kWh | Unit Energy Consumption
| [UEC_BaseFreezer] |  |  |  |  | 381 | N | kWh | Assumed consumption of a new baseline residential-sized freezer
| [WHFeHeatElectric] | [5 empty] | C |  | Waste Heat Factor for Energy to account for electric heating increase from removing waste heat from refrigerator/freezer (if fossil fuel heating – see calculation of heating penalty in that section).
| [HF] | Location | Heated Space |  |  | 54% | N |  | Heating factor or percentage of reduced waste heat that must now be heated
|  |  | Heated Space or Unknown |  |  | 0%
| [ηHeatElectric] | System Type | Heat Pump | Age of Equipment | Before 2006 | 2 | Y | COP | Efficiency in COP of Heating equipment
[5 empty] | 2006-2014 | 2.26
[5 empty] | 2015 on | 2.4
|  |  | Resistance |  |  | 1
|  |  | Unknown |  |  | 1.38
| [%ElecHeat] | Heating Fuel | Electric |  |  | 100% | N | % | Percentage of home with electric heat
|  |  | Fosil Fuel |  |  | 0%
|  |  | Unknown |  |  | 30%
| [WHFeCool] | [5 empty] | C |  | Waste Heat Factor for Energy to account for cooling savings from removing waste heat from refrigerator/freezer.
| [CoolF] | Cooling of Space | Cooling |  |  | 34% | N | % | Cooling Factor or percentage of reduced waste heat that no longer needs to be cooled
|  |  | No Cooling |  |  | 0%
| [ηCool] |  |  |  |  | 2.8 | Y | COP | Efficiency in COP of Cooling equipment
| [%Cool] | Cooling of Space | Cooling |  |  | 100% | N | % | Percentage of home with cooling
|  |  | No Cooling |  |  | 0%
|  |  | Unknown |  |  | 74%
| [ΔkW] |  |  |  |  | 0.1101 | C | kW | Deemed approach; Freezers
| [Hours] |  |  |  |  | 5895 | N |  | Equivalent Full Load Hours as calculated using eShapes loadprofile
| [WHFdCool] | Location | Cooled space |  |  | 1.29 | N |  | Waste heat factor for demand to account for cooling savings from removing waste heat.
|  |  | Uncooled space |  |  | 1
|  |  | Unknown space |  |  | 1.21
| [CF] |  |  |  |  | 95.3% | N |  | Coincident factor as calculated using eShapes loadprofile
| [WHFeHeatGas] | [5 empty] | C |  | Waste Heat Factor for Energy to account for gas heating increase from removing waste heat from refrigerator/freezer
| [ηHeatGas ] |  |  |  |  | 74% | N |  | Efficiency of heating system
| [%GasHeat] | Fuel Type | Electric |  |  | 0% | N |  | Percentage of homes with gas heat
|  |  | Gas |  |  | 100%
|  |  | Unknown |  |  | 70%
| [0.03412] |  |  |  |  | 0.03412 | N | kWh to Therms | Converts kWh to Therms
| [ΔTherms] | [5 empty] | C | Therms | Therm impact calcualted aboce
| [HeatDays] |  |  |  |  | 197 | N | Days | Heat season days per year

## Scroll Fridge Compressor
Scroll Fridge Compressor
| Measure Code: | NR-RFG-SCR-V02-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
12
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =((([Avg Cap] * [FLH])*(1 / [EER_base] - 1 / [EER_ee] ))) / [1000] * [units]
| Time of Sale Demand (ΔkW) | =[kWh] / [FLH] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Avg Cap] | [5 empty] | Y | Btu/h | Compressor capacity in Btu/h.
| [EERBase] | Temperature | Low Temperature (walk in freezers) | Capacity Bins in Btu/Hr | 0-4200 | 3.85 | N | Btu/watt hour | Cooling efficiency of existing compressor in Btu/watt-hour
[5 empty] | 4200-8399 | 4.83
[5 empty] | 8400-12599 | 5.06
[5 empty] | 12600-16799 | 5.26
[5 empty] | 16800-20999 | 5.36
[5 empty] | 21000-25199 | 5.69
[5 empty] | 25200-29399 | 5.71
[5 empty] | 29400-33599 | 6.14
[5 empty] | 33600-37800 | 5.64
[5 empty] | 37800-42000 | 5.73
|  |  | Medium Temperature (walk in coolers) |  | 0-7500 | 8.14
[5 empty] | 7500-14999 | 9.28
[5 empty] | 15000-22499 | 10.64
[5 empty] | 22500-29999 | 11.18
[5 empty] | 30000-37499 | 11.12
[5 empty] | 37500-44999 | 11.74
[5 empty] | 45000-52499 | 11.68
[5 empty] | 52500-59999 | 12.52
[5 empty] | 60000-67499 | 12.46
[5 empty] | 67500-75000 | 11.44
| [EERee] | Temperature | Low Temperature (walk in freezers) | Capacity Bins in Btu/Hr | 0-4200 | 4.39 | N | Btu/watt hour | Cooling efficiency of efficient scroll compressor in Btu/watt-hour.
[5 empty] | 4200-8399 | 5.21
[5 empty] | 8400-12599 | 5.37
[5 empty] | 12600-16799 | 5.59
[5 empty] | 16800-20999 | 5.8
[5 empty] | 21000-25199 | 6.06
[5 empty] | 25200-29399 | 6.15
[5 empty] | 29400-33599 | 6.39
[5 empty] | 33600-37800 | 6.06
[5 empty] | 37800-42000 | 6.06
|  |  | Medium Temperature (walk in coolers) |  | 0-7500 | 9.03
[5 empty] | 7500-14999 | 10.86
[5 empty] | 15000-22499 | 11.83
[5 empty] | 22500-29999 | 12.15
[5 empty] | 30000-37499 | 12.39
[5 empty] | 37500-44999 | 12.7
[5 empty] | 45000-52499 | 12.52
[5 empty] | 52500-59999 | 13.12
[5 empty] | 60000-67499 | 13.13
[5 empty] | 67500-75000 | 12.37
| [FLH] | Temperature | Medium Temperature (walk in coolers) |  |  | 3910 | N | Hours | Full load hours
|  |  | Low Temperature (walk in freezers) |  |  | 4139
| [Units] | [5 empty] | Y |  | Number of units installed
| [kWh] | [5 empty] | C | kWh | Gross customer connected load kWh savings for the measure
| [CF] |  |  |  |  | 96.4% | N |  | Summer peak coincidence factor

## Strip Curtain Walk in Cool Free
Strip Curtain for Walk-in Coolers and Freezers
| Measure Code: | NR-RFG-STCR-V03-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
4
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known |  | Actual
|  | Unknown |  | $10.22/ft2
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =(([Q_Base] / ([EER] × [1000])) - ([Q_EE] / ([EER] × [1000]))) × [EFLH]/ [A]× [A]
| Time of Sale Demand (ΔkW) | =([∆kWh] / [EFLH]) * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [Qbase] | Building Type | Grocery Store | Cooler or Freezer? | Cooler | 4661 | N | Btu/hr | Total infiltration load (Btu/hr) of cooler or freezer with no strip curtain installed
[5 empty] | Freezer | 7464
|  |  | Restaurant |  | Cooler | 1054
[5 empty] | Freezer | 2136
|  |  | Convenience Store |  | Cooler | 895
[5 empty] | Freezer | 485
|  |  | Unknown Building Type |  | Cooler | 2012
[5 empty] | Freezer | 3128
| [QEE] | Building Type | Grocery Store | Cooler or Freezer? | Cooler | 559 | N | Btu/hr | Total infiltration load (Btu/hr) of cooler or freezer with no strip curtain installed
[5 empty] | Freezer | 896
|  |  | Restaurant |  | Cooler | 211
[5 empty] | Freezer | 406
|  |  | Convenience Store |  | Cooler | 188
[5 empty] | Freezer | 82
|  |  | Unknown Building Type |  | Cooler | 355
[5 empty] | Freezer | 500
| [EER] | Building Type | Grocery Store | Cooler or Freezer? | Cooler | 10.6 | Y |  | Energy efficiency rato of cooler or freezer
[5 empty] | Freezer | 4.1
|  |  | Restaurant |  | Cooler | 9.8
[5 empty] | Freezer | 4
|  |  | Convenience Store |  | Cooler | 10.2
[5 empty] | Freezer | 4
| [1000] |  |  |  |  | 1000 | N | W to kW | Conversion factor from watts to kilowatts
| [EFLH] | Cooler or Freezer? | Cooler |  |  | 7693 | Y |  | Equivalent full load hours of cooler or freezer
|  |  | Freezer |  |  | 8121
| [A] |  |  |  |  | 21 | Y | ft2 | Area of cooler or freezer covered by strip curtains
| [ΔkWh] | [5 empty] | C | kWh | Electric energy savings, calculated above
| [CF] |  |  |  |  | 0.964 | N |  | Summer peak coincidence factor

## Ice Maker
Ice Maker
| Measure Code: | NR-RFG-ESIM-V02-190101
| Lifetime of Efficient Equipment: | [6 empty] | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
8
| Measure Cost: | [6 empty] | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Cost known? | Known |  |  | Actual
|  | Unknown | Equipment Type | Batch-Type | 0
|  |  |  | Continuous-Type | 222
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =[(([kWh_Base] - [kWh_ESTAR] )) / [100]] * ([Duty]* [H]) * [Days]
| Time of Sale Demand (ΔkW) | =[∆kWh] / ([Hours] * [Days])* [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Sub Algorithm
| [kWhBase] | Air-Cooled Batch-Type Ice Maker | IMH | Ice Harvest Rate | H< 300 | 10 - 0.01233*[H]
[5 empty] | 300 ≤ H < 800 | 7.05 – 0.0025*[H]
[5 empty] | 800 ≤ H < 1500 | 5.55 – 0.00063*[H]
[5 empty] | 1500 ≤ H ≤ 4000 | 4.61
|  |  | RCU |  | H< 988 | 7.97 – 0.00342*[H]
[5 empty] | 988 ≤ H ≤ 4000 | 4.59
|  |  | SCU |  | H< 110 | 14.79 - 0.0469*[H]
[5 empty] | 110 ≤ H < 200 | 12.42 - 0.02533*[H]
[5 empty] | 200 ≤ H ≤ 4000 | 7.35
|  | Air-Cooled Continuous-Type Ice Maker | IMH |  | H< 310 | 9.19 - 0.00629*[H]
[5 empty] | 310 ≤ H < 820 | 8.23 - 0.0032*[H]
[5 empty] | 820 ≤ H ≤ 4000 | 5.61
|  |  | RCU |  | H< 800 | 9.7 - 0.0058*[H]
[5 empty] | 800 ≤ H ≤ 4000 | 5.06
|  |  | SCU |  | H< 200 | 14.22 - 0.03*[H]
[5 empty] | 200 ≤ H < 700 | 9.47 - 0.00624*[H]
[5 empty] | 700 ≤ H ≤ 4000 | 5.1
| [kWhESTAR] | Air-Cooled Batch-Type Ice Maker | IMH | Ice Harvest Rate | H< 300 | ≤ 9.20 - 0.01134*[H]
[5 empty] | 300 ≤ H < 800 | ≤ 6.49 - 0.0023*[H]
[5 empty] | 800 ≤ H < 1500 | ≤ 5.11 - 0.00058*[H]
[5 empty] | 1500 ≤ H ≤ 4000 | ≤ 4.24
|  |  | RCU |  | H< 988 | ≤ 7.17 - 0.00308*[H]
[5 empty] | 988 ≤ H ≤ 4000 | ≤ 4.13
|  |  | SCU |  | H< 110 | ≤ 12.57 - 0.0399*[H]
[5 empty] | 110 ≤ H < 200 | ≤ 10.56 - 0.0215*[H]
[5 empty] | 200 ≤ H ≤ 4000 | ≤ 6.25
|  | Air-Cooled Continuous-Type Ice Maker | IMH |  | H< 310 | ≤ 7.90 - 0.005409*[H]
[5 empty] | 310 ≤ H < 820 | ≤ 7.08 - 0.002752*[H]
[5 empty] | 820 ≤ H ≤ 4000 | ≤ 4.82
|  |  | RCU |  | H< 800 | ≤ 7.76 - 0.00464*[H]
[5 empty] | 800 ≤ H ≤ 4000 | ≤ 4.05
|  |  | SCU |  | H< 200 | ≤ 12.37 - 0.0261*[H]
[5 empty] | 200 ≤ H < 700 | ≤ 8.24 - 0.005429*[H]
[5 empty] | 700 ≤ H ≤ 4000 | ≤ 4.44
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [kWhBase] | [5 empty] | C | kwh / 100 lbs | Energy consumption rate (kWh / 100 pounds of ice) of baseline ice maker
| [kWhESTAR] | [5 empty] | C | kwh / 100 lbs | Energy consumption rate (kWh / 100 pounds of ice) of ENERGY STAR ice maker
| [100] |  |  |  |  | 100 | N |  | Factor to convert kWhBase and kWhESTAR into energy consumption per pound of ice
| [Duty] |  |  |  |  | 0.75 | Y |  | Duty cycle (%) of ice maker
| [H] | Air-Cooled Batch Type | IMH |  |  | 650 | Y | lbs of ice/day | Ice harvest rate (pounds of ice/day)
|  |  | RCU |  |  | 1150
|  |  | SCU |  |  | 170
|  | Air-Cooled Continuous-Type | IMH |  |  | 680
|  |  | RCU |  |  | 1170
|  |  | SCU |  |  | 240
| [Days] |  |  |  |  | 365.25 | Y | Days | Annual days of operation
| [ΔkWh] | [5 empty] | C | kWh | Electric energy savings, calculated above
| [Hours] |  |  |  |  | 12 | Y | Hours | Average daily hours of operation
| [CF] |  |  |  |  | 0.964 | N |  | Summer peak coincidence factor

## Eff Motor Contr Walk-in Display
Efficient Motor Controls for Walk-In and Display Case Coolers/Freezers
| Measure Code: | NR-RFG-ECMC-V01-190101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
16
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
291
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | =((5988.5*[kW_Output])+63.875)*[#Motors]
| Time of Sale Demand (ΔkW) | =([∆kWh] / [Hours])*[CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [kW_Output] |  |  |  |  | 0.01495 | Y | kW | Output wattage of installed fan motor
| [#Motors] | [5 empty] | Y |  | Number of fan motors controlled
| [ΔkWh] | [5 empty] | C | kWh | Electric energy savings, calculated above
| [Hours] |  |  |  |  | 8766 | N | Hours | Annual hours of cooler or freezer operation
| [CF] |  |  |  |  | 0.964 | N |  | Summer peak coincidence factor

## Add Doors to Display Cases
Adding Doors to Open Refrigerated Display Cases
| Measure Code: | NR-RFG-DOOR-V01-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
12
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
522
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = (([ΔHG] * [CL]) / ([EER] * [1000]) * [8760]) + ([MMBtuHVACCool] * [CL] * (1 / [SEER]) * [1000])
| Time of Sale Demand (ΔkW) | = (([ΔHG] * [CL]) / ([EER] * [1000]) * [CFRefrigeration]) + ((MMBtuHVACCool] / [HoursCool] * [CL] * (1 / [SEER]) * [1000]) * [CFCool])
| Time of Sale Gas (ΔTherms) | = [MMBtuHVACHeat] * [CL] * (1 / [AFUE]) * [10]
| Time of Sale Peak Gas (ΔPeakTherms) | = [ΔTherms] * [GCF]
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [ΔHG] |  |  |  |  | 1148 | N | Btu/h-ft | Heat Gain, the decreased load or the reduced heat gain on the open refrigerated display case with the installation of a door (Btu/hr-linear foot)
| [CL] | [5 empty] | Y | Number | Case Length, refrigerated case length in feet
| [EER] |  |  |  |  | 11.36 | Y | Btu/hr-watt | Energy Efficiency Ratio; display case compressor efficiency (Btu/hr-watt)
| [1000] |  |  |  |  | 1000 | N | W/kW | Conversion from watts to kilowatts (W / kW)
| [8760] |  |  |  |  | 8760 | N | Hours | Annual operating hours of the refrigerated display case
| [MMBtuHVACCool] |  |  |  |  | -2.789 | N | MMBtu/ft | Total cooling load increase on the HVAC equipment per linear foot of display case
| [SEER] |  |  |  |  | 13 | Y | Btu/hr-watt | Seasonal Energy Efficiency Ratio; HVAC equipment operating efficiency (Btu/hr-watt)
| [HoursCool] |  |  |  |  | 3329 | N | Hours | Total combined hours the site is providing cooling
| [CFRefrigeration] |  |  |  |  | 0.964 | N |  | Summer peak coincidence factor for the refrigerated display case
| [CF] | Building Type | Convenience |  |  | 92.3% | N |  | Summer peak coincidence factor for the HVAC cooling system (dependent on building type)
|  |  | Education |  |  | 96.7%
|  |  | Grocery |  |  | 100%
|  |  | Health |  |  | 100%
|  |  | Hospital |  |  | 98.6%
|  |  | Industrial |  |  | 44.6%
|  |  | Lodging |  |  | 97.4%
|  |  | Multifamily |  |  | 100%
|  |  | Office - Large |  |  | 98.8%
|  |  | Office - Small |  |  | 100%
|  |  | Religious |  |  | 94.3%
|  |  | Restaurant |  |  | 99.6%
|  |  | Retail - Large |  |  | 87.6%
|  |  | Retail - Small |  |  | 100%
|  |  | Warehouse |  |  | 77.9%
|  |  | Nonresidential Average |  |  | 92.3%
| [MMBtuHVACHeat] |  |  |  |  | 4.754 | N | MMBtu/ft | Total heating load decrease on the HVAC equipment per linear foot of display case
| [AFUE] |  |  |  |  | 0.8 | Y |  | Typical heating system efficiency of 80%, consistent with current heating efficiency assumptions for lighting HVAC interactive effects for commercial fossil fuel-fired systems.
| [10] |  |  |  |  | 10 | N | therms/MMBtu | Conversion from MMBtu to therms
| [GCF] | Building Type | Convenience |  |  | 0.016482 | N |  | Gas Coincidence Factor for Heating
|  |  | Education |  |  | 0.01148
|  |  | Grocery |  |  | 0.013083
|  |  | Health |  |  | 0.010179
|  |  | Hospital |  |  | 0.015543
|  |  | Industrial |  |  | 0.014296
|  |  | Lodging |  |  | 0.013205
|  |  | Multifamily |  |  | 0.012268
|  |  | Office - Large |  |  | 0.013082
|  |  | Office - Small |  |  | 0.016718
|  |  | Religious |  |  | 0.011964
|  |  | Restaurant |  |  | 0.015262
|  |  | Retail - Large |  |  | 0.013281
|  |  | Retail - Small |  |  | 0.014055
|  |  | Warehouse |  |  | 0.015677
|  |  | Nonresidential Average |  |  | 0.014658

## Refrigeration Economizers
Refrigeration Economizers
| Measure Code: | NR-RFG-ECON-V01-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
Actual
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [kWh Savings]
| Time of Sale Demand (ΔkW) | = 0
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| [kWh Savings] | Auxiliary Circulator Fan and Controlls | Installed | = ([HP] * [kWhCond]) + ((([kWEvap] * [nFans] * [DCComp] * [BF]) – [kWCirc] – ([kWEcon] * [DCEcon])) * [Hours])
|  |  | Not Installed | = ([HP] * [kWhCond]) – ([kWEcon] * [DCEcon] * [Hours])
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [HP] | [5 empty] | Y | Hp | Horsepower of compressor
| [kWhCond] | Climate Zone | Zone 5 (Burlington) | Compressor Type | Hermetic/Semi-Hermetic | 758 | C | kWh | Condensing unit savings, per hp. Based on climate zone and compressor type
[5 empty] | Scroll | 665
[5 empty] | Discus | 629
|  |  | Zone 6 (Mason City) |  | Hermetic/Semi-Hermetic | 1149
[5 empty] | Scroll | 1009
[5 empty] | Discus | 995
|  |  | Average/Unknown |  | Hermetic/Semi-Hermetic | 815
[5 empty] | Scroll | 716
[5 empty] | Discus | 667
| [Hours] | Climate Zone | Zone 5 (Burlington) |  |  | 1877 | N | Hours | Number of annual hours that economizer operates
|  |  | Zone 6 (Mason City) |  |  | 2848
|  |  | Average/Unknown |  |  | 2020
| [DCComp] |  |  |  |  | 0.5 | N |  | Duty cycle of the compressor
| [kWEvap] |  |  |  |  | 0.123 | Y | kW | Connected load kW of each evaporator fan
| [kWCirc] |  |  |  |  | 0.035 | Y | kW | Connected load kW of the circulating fan
| [nFans] | [5 empty] | Y | Number | Number of evaporator fans
| [DCEcon] |  |  |  |  | 0.63 | Y |  | Duty cycle of the economizer fan on days that are cool enough for the economizer to be working
| [BF] |  |  |  |  | 1.3 | N |  | Bonus factor for reduced cooling load attributed to removing waste heat from evaporator fans. Dedicated high-efficiency circulator fans require less power and use high efficiency motors, resulting in less waste heat.
| [kWEcon] |  |  |  |  | 0.227 | Y | kW | Connected load kW of the economizer fan(s)

## Air Compressor with VSD
Air Compressor with VSD
| Measure Code: | NR-MSC-VSDA-V01-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
13
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
See Sub-Algorithm
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [0.9] * [HPcompressor] * [Hours] * ([CFb] - [CFe])
| Time of Sale Demand (ΔkW) | = [∆kWh] / [Hours] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
| Incremental Cost |  |  | = ([$127] * [HPcompressor]) + [$1446]
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [$127] |  |  |  |  | 127 | N | $ | Compressor motor nominal hp to incremental cost conversion factor
| [$1446] |  |  |  |  | 1446 | N | $ | Compressor motor nominal hp to incremental cost offset
| [0.9] |  |  |  |  | 0.9 | N | kW/hp | compressor motor nominal hp to full load kW conversion factor
| [HPcompressor] | [5 empty] | Y | Hp | compressor motor nominal hp
| [Hours] | Shift Type | Single-Shift (8/5) |  |  | 1976 | Y | Hours | compressor total hours of operation depending on shift
|  |  | 2-Shift (16/5) |  |  | 3952
|  |  | 3-Shift (24/5) |  |  | 5928
|  |  | 4-Shift (24/7) |  |  | 8320
|  |  | Unknown/Weighted Average |  |  | 5680
| [CFb] | Compressor Size | ≤ 40 Hp | Compressor Type | Modulating w/ Blowdown | 0.89 | N |  | baseline compressor factor
[5 empty] | Load/No Load w/ 1 Gallon/CFM | 0.909
[5 empty] | Load/No Load w/ 3 Gallon/CFM | 0.831
[5 empty] | Load/No Load w/ 5 Gallon/CFM | 0.806
|  |  | 50 - 200 Hp |  | Modulating w/ Blowdown | 0.863
[5 empty] | Load/No Load w/ 1 Gallon/CFM | 0.887
[5 empty] | Load/No Load w/ 3 Gallon/CFM | 0.811
[5 empty] | Load/No Load w/ 5 Gallon/CFM | 0.786
| [CFe] | Compressor Size | ≤ 40 Hp |  |  | 0.705 | N |  | efficient compressor factor
|  |  | 50 - 200 Hp |  |  | 0.658
| [CF] | Shift Type | Single-Shift (8/5) |  |  | 0 | N |  | Summer peak coincidence factor
|  |  | 2-Shift (16/5) |  |  | 0.95
|  |  | 3-Shift (24/5) |  |  | 0.95
|  |  | 4-Shift (24/7) |  |  | 0.95
|  |  | Unknown/Weighted Average |  |  | 0.8

## High Efficiency Air Nozzle
High Efficiency Air Nozzle
| Measure Code: | NR-MSC-ACNZ-V01-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
15
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
| Orifice Diameter | 1/8" | 42
|  | 1/4" | 57
|  | 5/16" | 87
|  | 1/2" | 121
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [SCFM_Baseline] * [SCFM_Efficient] * [%Use] * [kW/CFM_Saved] * [Hours]
| Time of Sale Demand (ΔkW) | = ∆kWh / [Hours] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [SCFM_Baseline] | Orifice Diameter | 1/8" |  |  | 21 | Y | SCFM | Air flow through baseline nozzle. Use actual rated flow at 80 psi if known
|  |  | 1/4" |  |  | 58
|  |  | 5/16" |  |  | 113
|  |  | 1/2" |  |  | 280
| [SCFM_Efficient] | Orifice Diameter | 1/8" |  |  | 10.5 | Y | SCFM | Air flow through the efficient nozzle. Use actual rated flow rate at 80 psi if known
|  |  | 1/4" |  |  | 29
|  |  | 5/16" |  |  | 56.5
|  |  | 1/2" |  |  | 140
| [%Use] |  |  |  |  | 0.05 | N |  | Percent of the compressor total operating hours that the nozzle is in use
| [kW/CFM_Saved] | Air Compressor Type |  |  |  | 0.184 | N | kW/CFM | System power reduction per reduced air demand (kW/CFM), depending on the type of air compressor
0.136
0.152
0.055
0.055
0.153
0.178
0.107
| [Hours] | Shift Type | Single-Shift (8/5) |  |  | 1976 | Y | Hours | compressor total hours of operation depending on shift
|  |  | 2-Shift (16/5) |  |  | 3952
|  |  | 3-Shift (24/5) |  |  | 5928
|  |  | 4-Shift (24/7) |  |  | 8320
|  |  | Unknown/Weighted Average |  |  | 5680
| [CF] | Shift Type | Single-Shift (8/5) |  |  | 0 | N |  | Summer peak coincidence factor
|  |  | 2-Shift (16/5) |  |  | 0.95
|  |  | 3-Shift (24/5) |  |  | 0.95
|  |  | 4-Shift (24/7) |  |  | 0.95
|  |  | Unknown/Weighted Average |  |  | 0.8

## No Loss Condensate Drain
No Loss Condensate Drain
| Measure Code: | NR-MSC-NLCD-V01-210101
| Lifetime of Efficient Equipment: |  |  |  |  | Remaining Lifetime of Existing Equipment (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Lifetime |  |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Remaining Lifetime
13
| Measure Cost: |  |  |  |  | Deferred Baseline Replacement Cost (Early Replacement Only):
| Dependent Variable Input 1 | Dependent Variable 1 Options | Incremental Cost | Full Cost (Early Replacement) |  | Dependent Variable Input 1 | Dependent Variable 1 Options | Deferred Baseline Replacement Cost
244
O&M Cost:
| Dependent Variable Input 1 | Dependent Variable 1 Options | Life of Component | Cost
Primary Algorithms:
| Metric | Algorithm
Time of Sale | Time of Sale Energy (ΔkWh) | = [CFM_Reduced] * [kW/CFM_Saved] * [Hours]
| Time of Sale Demand (ΔkW) | = ΔkWh / [Hours] * [CF]
Time of Sale Gas (ΔTherms)
Time of Sale Peak Gas (ΔPeakTherms)
Time of Sale Water (ΔGallons)
Early Replacement Only | Existing Unit Life Energy (ΔkWh)
Existing Unit Life Demand (ΔkW)
Existing Unit Life Gas (ΔTherms)
Existing Unit Life Peak Gas (ΔPeakTherms)
Existing Unit Life Water (ΔGallons)
Remaining Life Energy (ΔkWh)
Remaining Life Demand (ΔkW)
Remaining Life Gas (ΔTherms)
Remaining Life Peak Gas (ΔPeakTherms)
Remaining Life Water (ΔGallons)
Sub Algorithms:
| Variable | Dependent Variable Input 1 | Dependent Variable 1 Options | Sub Algorithm
Variables:
| Label | Dependent Variable Input 1 | Dependent Variable 1 Options | Dependent Variable Input 2 | Dependent Variable 2 Options | Defaults / Values | Calculation (C) or Customizable (Y/N) | Units | Variable Definition
| [CFM_Reduced] |  |  |  |  | 3 | N | CFM | Reduced air consumption per drain
| [kW/CFM_Saved] | Air Compressor Type |  |  |  | 0.184 | N | kW/CFM | System power reduction per reduced air demand (kW/CFM), depending on the type of air compressor
0.136
0.152
0.055
0.055
0.153
0.178
0.107
| [Hours] |  |  |  |  | 6136 | N | Hours | Compressed air system pressurized hours
| [CF] |  |  |  |  | 0.95 | N |  | Summer peak coincidence factor